## README
PRAESENSA
Power calculator V1.3
语言 / Sprache / Language / Langue / Lingua / Taal |  | English
USER INSTRUCTIONS
1. Start by selecting the required language above.
2. All yellow marked cells are drop down input fields (click on it).
3. When the text in these yellow cells is red the data has to be typed in.
4. Select the INFO tab and type in the date, project name and battery operation requirements.
5. Select per cluster the tab at the bottom and fill in the required data.
6. Result per cluster is displayed in the INFO tab including heat loss of the complete rack.
This tool calculates the power requirements for a PRAESENSA system. It calculates up to 6 clusters. A cluster consists of one PRA-MPS3 and the connected devices to be supplied with power. Use the safety factor in the calculation of the battery capacity to compensate the tolerances of battery brands and types. Please also check the rack space requirements for the calculated battery types. For each additional rack a new calculation has to be made.
Special Note: Maximum battery current must be observed while it highly varies among different battery types.
The Power calculator serves as a support tool only. It cannot substitute professional advice from technical experts. For further details, our sales and support team will be happy to assist. Bosch does not warrant that the tool will fulfill any specific or general user requirement and disclaims any warranty for fitness for a specific purpose. To the extent permitted by law, Bosch will not accept any liability for any loss, damage or other consequences resulting from the use of the tool.

## INFO
PRAESENSA
Power calculator V1.3
Date: | 2024-02-14
Project: | BOSCH 1
Battery Operation Requirements
Time in quiescent condition |  |  | 24 | hour | When the system is powered by a power supply conforming to EN 54-4 and no other functional condition is indicated.
Time in evacuation condition |  |  | 30 | min. | Maximum time interval the voice alarm system must be used for evacuation.
Safety factor (tolerance, temperature) |  |  | 30 | % | Additional battery capacity to compensate for aging and low temperature operation, appr. 10%, as well as reduced capacity, appr. 20%, due to fast discharge of the battery (Peukert's law).
Cluster > | [7 empty] | 1 | 2 | 3 | 4 | 5 | 6
Required battery capacity including safety factor (minimum 100 Ah - maximum 230 Ah) | [6 empty] | Ah | 0 | 0 | 0 | 0 | 0 | 0
Maximum battery current (check battery specification) | [6 empty] | A | 0 | 0 | 0 | 0 | 0 | 0
Mains current draw at 230 VAC (during alarm and bulk charging) | [6 empty] | A | 0 | 0 | 0 | 0 | 0 | 0
Mains current draw at 115 VAC (during alarm and bulk charging) | [6 empty] | A | 0 | 0 | 0 | 0 | 0 | 0
Total heat loss (heat dissipation inside the rack)*
|  |  | Idle |  | Low power | Full power
|  | W | 0 |  | 0 | 0
|  | BTU/h | 0 |  | 0 | 0
|  | kcal/h | 0 |  | 0 | 0
* Excluding call stations and 3rd party devices
For more information about battery and heat loss calculation please read the applicable sections in chapter "System composition" of the PRAESENSA Installation manual.
This tool calculates the power requirements for a PRAESENSA system. It calculates up to 6 clusters. A cluster consists of one PRA-MPS3 and the connected devices to be supplied with power. Use the safety factor in the calculation of the battery capacity to compensate the tolerances of battery brands and types. Please also check the rack space requirements for the calculated battery types. For each additional rack a new calculation has to be made.
Special Note: Maximum battery current must be observed while it highly varies among different battery types.
The Power calculator serves as a support tool only. It cannot substitute professional advice from technical experts. For further details, our sales and support team will be happy to assist. Bosch does not warrant that the tool will fulfill any specific or general user requirement and disclaims any warranty for fitness for a specific purpose. To the extent permitted by law, Bosch will not accept any liability for any loss, damage or other consequences resulting from the use of the tool.

## CLUSTER_1
PRAESENSA
Power calculator V1.3
Cluster 1 |  | Used: | NO
Description | Device |  |  | Required battery capacity including safety factor (minimum 100 Ah - maximum 230 Ah) |  |  |  | -
Supported battery capacity is between 100Ah and 230Ah!
2
0
|  |  |  | Maximum battery current (check battery specification) |  |  |  | -
-
|  |  | 1 | The maximum battery current of 90A is exceeded!
-
|  |  | 1 | Mains current draw at 230 VAC (during alarm and bulk charging) |  |  |  | -
0
0
-
|  |  | 1 | Mains current draw at 115 VAC (during alarm and bulk charging) |  |  |  | -
0
0
-
|  |  | 8 | WRONG DATA ENTRIE(S) > CHECK ALL QUANTITIES !!!
0
0
NO
1
0
0
1
|  |  | 0 |  | Total heat loss*
|  |  | NO |  |  | Idle | Low power | Full power
1
[5 empty] | W | - | - | -
NO
|  |  | 1 |  | BTU/h | - | - | -
|  |  | NO |  | kcal/h | - | - | -
1
* Excluding call stations and 3rd party devices
This tool calculates the power requirements for a PRAESENSA system. It calculates up to 6 clusters. A cluster consists of one PRA-MPS3 and the connected devices to be supplied with power. Use the safety factor in the calculation of the battery capacity to compensate the tolerances of battery brands and types. Please also check the rack space requirements for the calculated battery types. For each additional rack a new calculation has to be made.
Special Note: Maximum battery current must be observed while it highly varies among different battery types.
The Power calculator serves as a support tool only. It cannot substitute professional advice from technical experts. For further details, our sales and support team will be happy to assist. Bosch does not warrant that the tool will fulfill any specific or general user requirement and disclaims any warranty for fitness for a specific purpose. To the extent permitted by law, Bosch will not accept any liability for any loss, damage or other consequences resulting from the use of the tool.

## CLUSTER_2
PRAESENSA
Power calculator V1.3
Cluster 2 |  | Used: | NO
Description | Device |  |  | Required battery capacity including safety factor (minimum 100 Ah - maximum 230 Ah) |  |  |  | -
Supported battery capacity is between 100Ah and 230Ah!
2
0
|  |  |  | Maximum battery current (check battery specification) |  |  |  | -
-
|  |  | 1 | The maximum battery current of 90A is exceeded!
-
|  |  | 1 | Mains current draw at 230 VAC (during alarm and bulk charging) |  |  |  | -
0
0
-
|  |  | 1 | Mains current draw at 115 VAC (during alarm and bulk charging) |  |  |  | -
0
0
-
|  |  | 1 | WRONG DATA ENTRIE(S) > CHECK ALL QUANTITIES !!!
0
0
NO
1
0
0
1
|  |  | 0 |  | Total heat loss*
|  |  | NO |  |  | Idle | Low power | Full power
1
[5 empty] | W | - | - | -
NO
|  |  | 1 |  | BTU/h | - | - | -
|  |  | NO |  | kcal/h | - | - | -
1
* Excluding call stations and 3rd party devices
This tool calculates the power requirements for a PRAESENSA system. It calculates up to 6 clusters. A cluster consists of one PRA-MPS3 and the connected devices to be supplied with power. Use the safety factor in the calculation of the battery capacity to compensate the tolerances of battery brands and types. Please also check the rack space requirements for the calculated battery types. For each additional rack a new calculation has to be made.
Special Note: Maximum battery current must be observed while it highly varies among different battery types.
The Power calculator serves as a support tool only. It cannot substitute professional advice from technical experts. For further details, our sales and support team will be happy to assist. Bosch does not warrant that the tool will fulfill any specific or general user requirement and disclaims any warranty for fitness for a specific purpose. To the extent permitted by law, Bosch will not accept any liability for any loss, damage or other consequences resulting from the use of the tool.

## CLUSTER_3
PRAESENSA
Power calculator V1.3
Cluster 3 |  | Used: | NO
Description | Device |  |  | Required battery capacity including safety factor (minimum 100 Ah - maximum 230 Ah) |  |  |  | -
Supported battery capacity is between 100Ah and 230Ah!
2
0
|  |  |  | Maximum battery current (check battery specification) |  |  |  | -
-
|  |  | 1 | The maximum battery current of 90A is exceeded!
-
|  |  | 1 | Mains current draw at 230 VAC (during alarm and bulk charging) |  |  |  | -
0
0
-
|  |  | 1 | Mains current draw at 115 VAC (during alarm and bulk charging) |  |  |  | -
0
0
-
|  |  | 1 | WRONG DATA ENTRIE(S) > CHECK ALL QUANTITIES !!!
0
0
NO
1
0
0
1
|  |  | 0 |  | Total heat loss*
|  |  | NO |  |  | Idle | Low power | Full power
1
[5 empty] | W | - | - | -
NO
|  |  | 1 |  | BTU/h | - | - | -
|  |  | NO |  | kcal/h | - | - | -
1
* Excluding call stations and 3rd party devices
This tool calculates the power requirements for a PRAESENSA system. It calculates up to 6 clusters. A cluster consists of one PRA-MPS3 and the connected devices to be supplied with power. Use the safety factor in the calculation of the battery capacity to compensate the tolerances of battery brands and types. Please also check the rack space requirements for the calculated battery types. For each additional rack a new calculation has to be made.
Special Note: Maximum battery current must be observed while it highly varies among different battery types.
The Power calculator serves as a support tool only. It cannot substitute professional advice from technical experts. For further details, our sales and support team will be happy to assist. Bosch does not warrant that the tool will fulfill any specific or general user requirement and disclaims any warranty for fitness for a specific purpose. To the extent permitted by law, Bosch will not accept any liability for any loss, damage or other consequences resulting from the use of the tool.

## CLUSTER_4
PRAESENSA
Power calculator V1.3
Cluster 4 |  | Used: | NO
Description | Device |  |  | Required battery capacity including safety factor (minimum 100 Ah - maximum 230 Ah) |  |  |  | -
Supported battery capacity is between 100Ah and 230Ah!
2
0
|  |  |  | Maximum battery current (check battery specification) |  |  |  | -
-
|  |  | 1 | The maximum battery current of 90A is exceeded!
-
|  |  | 1 | Mains current draw at 230 VAC (during alarm and bulk charging) |  |  |  | -
0
0
-
|  |  | 1 | Mains current draw at 115 VAC (during alarm and bulk charging) |  |  |  | -
0
0
-
|  |  | 1 | WRONG DATA ENTRIE(S) > CHECK ALL QUANTITIES !!!
0
0
NO
1
0
0
1
|  |  | 0 |  | Total heat loss*
|  |  | NO |  |  | Idle | Low power | Full power
1
[5 empty] | W | - | - | -
NO
|  |  | 1 |  | BTU/h | - | - | -
|  |  | NO |  | kcal/h | - | - | -
1
* Excluding call stations and 3rd party devices
This tool calculates the power requirements for a PRAESENSA system. It calculates up to 6 clusters. A cluster consists of one PRA-MPS3 and the connected devices to be supplied with power. Use the safety factor in the calculation of the battery capacity to compensate the tolerances of battery brands and types. Please also check the rack space requirements for the calculated battery types. For each additional rack a new calculation has to be made.
Special Note: Maximum battery current must be observed while it highly varies among different battery types.
The Power calculator serves as a support tool only. It cannot substitute professional advice from technical experts. For further details, our sales and support team will be happy to assist. Bosch does not warrant that the tool will fulfill any specific or general user requirement and disclaims any warranty for fitness for a specific purpose. To the extent permitted by law, Bosch will not accept any liability for any loss, damage or other consequences resulting from the use of the tool.

## CLUSTER_5
PRAESENSA
Power calculator V1.3
Cluster 5 |  | Used: | NO
Description | Device |  |  | Required battery capacity including safety factor (minimum 100 Ah - maximum 230 Ah) |  |  |  | -
Supported battery capacity is between 100Ah and 230Ah!
2
0
|  |  |  | Maximum battery current (check battery specification) |  |  |  | -
-
|  |  | 1 | The maximum battery current of 90A is exceeded!
-
|  |  | 1 | Mains current draw at 230 VAC (during alarm and bulk charging) |  |  |  | -
0
0
-
|  |  | 1 | Mains current draw at 115 VAC (during alarm and bulk charging) |  |  |  | -
0
0
-
|  |  | 1 | WRONG DATA ENTRIE(S) > CHECK ALL QUANTITIES !!!
0
0
NO
1
0
0
1
|  |  | 0 |  | Total heat loss*
|  |  | NO |  |  | Idle | Low power | Full power
1
[5 empty] | W | - | - | -
NO
|  |  | 1 |  | BTU/h | - | - | -
|  |  | NO |  | kcal/h | - | - | -
1
* Excluding call stations and 3rd party devices
This tool calculates the power requirements for a PRAESENSA system. It calculates up to 6 clusters. A cluster consists of one PRA-MPS3 and the connected devices to be supplied with power. Use the safety factor in the calculation of the battery capacity to compensate the tolerances of battery brands and types. Please also check the rack space requirements for the calculated battery types. For each additional rack a new calculation has to be made.
Special Note: Maximum battery current must be observed while it highly varies among different battery types.
The Power calculator serves as a support tool only. It cannot substitute professional advice from technical experts. For further details, our sales and support team will be happy to assist. Bosch does not warrant that the tool will fulfill any specific or general user requirement and disclaims any warranty for fitness for a specific purpose. To the extent permitted by law, Bosch will not accept any liability for any loss, damage or other consequences resulting from the use of the tool.

## CLUSTER_6
PRAESENSA
Power calculator V1.3
Cluster 6 |  | Used: | NO
Description | Device |  |  | Required battery capacity including safety factor (minimum 100 Ah - maximum 230 Ah) |  |  |  | -
Supported battery capacity is between 100Ah and 230Ah!
2
0
|  |  |  | Maximum battery current (check battery specification) |  |  |  | -
-
|  |  | 1 | The maximum battery current of 90A is exceeded!
-
|  |  | 1 | Mains current draw at 230 VAC (during alarm and bulk charging) |  |  |  | -
0
0
-
|  |  | 1 | Mains current draw at 115 VAC (during alarm and bulk charging) |  |  |  | -
0
0
-
|  |  | 1 | WRONG DATA ENTRIE(S) > CHECK ALL QUANTITIES !!!
0
0
NO
1
0
0
1
|  |  | 0 |  | Total heat loss*
|  |  | NO |  |  | Idle | Low power | Full power
1
[5 empty] | W | - | - | -
NO
|  |  | 1 |  | BTU/h | - | - | -
|  |  | NO |  | kcal/h | - | - | -
1
* Excluding call stations and 3rd party devices
This tool calculates the power requirements for a PRAESENSA system. It calculates up to 6 clusters. A cluster consists of one PRA-MPS3 and the connected devices to be supplied with power. Use the safety factor in the calculation of the battery capacity to compensate the tolerances of battery brands and types. Please also check the rack space requirements for the calculated battery types. For each additional rack a new calculation has to be made.
Special Note: Maximum battery current must be observed while it highly varies among different battery types.
The Power calculator serves as a support tool only. It cannot substitute professional advice from technical experts. For further details, our sales and support team will be happy to assist. Bosch does not warrant that the tool will fulfill any specific or general user requirement and disclaims any warranty for fitness for a specific purpose. To the extent permitted by law, Bosch will not accept any liability for any loss, damage or other consequences resulting from the use of the tool.

## CALC_1 (hidden)
0
1 |  |  | Yellow marked cells are updated in v1.2
2 |  |  | Orange marked cells are updated in v1.3
3
4 |  | Single device battery current [mA] |  |  |  |  | All device battery current [mA] |  |  |  | Device count |  |  | Mains current [mA]
5 |  |  | Quiescent | Alarm (max) |  | Quantity |  | Quiescent | Alarm (max) |  | MPS Out 1 | MPS Out 2 | MPS Out 3 | Battery max. charging
6 | PRA-MPS3 |  | 430 | 430 |  | 0 |  | 0 | 0 |  |  |  |  | 567.3913
7 | MPS3 Ethernet port |  | 30 | 30 |  | 0 |  | 0 | 0
8 | MPS3 SFP port |  | 60 | 60 |  | 0 |  | 0 | 0
9
10 | PRA-SCx |  | 350 | 350 |  | 0 |  | 0 | 0
11 | SCx Ethernet port |  | 40 | 40 |  | 0 |  | 0 | 0
12
13 | 3rd-Party (on 24V output) |  | 0 | 0 |  | 0 |  | 0 | 0
14 | [13 empty] | Max. current [mA]
15 | PRA-AD604 |  | 670 |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 1060.6957
16 | Amp. Ethernet ports |  | 30 | 30 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0
17 | Total LSP load |  |  |  |  | 0 |  |  |  |  | 0 | 0 | 0
18 | PRA-AD608 |  | 790 |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 1178.087
19 | Amp. Ethernet ports |  | 30 | 30 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0
20 | Total LSP load |  |  |  |  | 0 |  |  |  |  | 0 | 0 | 0
21 | PRA-ES8P2S |  | 700 | 700 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0
22 | Active Ethernet ports |  | 40 | 40 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0
23 | Active SFP ports |  | 70 | 70 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0
24 | PoE load |  |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0
25 | 3rd-Party 1 (on 48V output) |  | 0 | 0 |  | 0 |  | 0 | 0
26 | 3rd-Party 2 (on 48V output) |  | 0 | 0 |  | 0 |  | 0 | 0
27 | 3rd-Party 3 (on 48V output) |  | 0 | 0 |  | 0 |  | 0 | 0
28
29 | PRA-CSLD |  | 420 | 420 |  | 0 |  | 0 | 0
30 | PRA-CSLW |  | 420 | 420 |  | 0 |  | 0 | 0
31 | PRA-CSE |  | 10 | 10 |  | 0 |  | 0 | 0 |  |  | 0 | PoE port(s) minimal required
32 | CS PoE port |  | 50 | 50 |  | 0 |  | 0 | 0 |  |  | 0 | PoE port(s) available without ANS
33 | CS Alarm option |  | 120 | 120 |  | 0 |  | 0 | 0
34
35 | PRA-ANS |  | 158 | 158 |  | 0 |  | 0 | 0 |  |  | 0 | PoE port(s) available with ANS
36
37 | PRA-IM16C8 |  | 370 | 370 |  | 0 |  | 0 | 0 |  |  | 0 | PoE port(s) available with IM16C8
38
39 | PRA-WCP-xx |  | 130 | 130 |  | 0 |  | 0 | 0 |  |  | 0 | PoE port(s) available with WCP-xx
40
41 | [5 empty] | 0 |  | 0 | 0
42 |  |  |  |  | Without MPS: | 0 |  | 0 | 0
43
44 |  |  | Selected quantity check |  |  | 0
45 |  |  |  | Quantity check MPS |  | FALSE
46 |  |  |  | Quantity check CSLx |  | FALSE
47
48
49 | Device | Battery capacity [Ah] |  | Total [Ah] | Mains current [mA] |  |  | Total heat loss
50 |  | Quiescent | Alarm |  | Single | Total
51 | PRA-MPS3 | 0 | 0 | 0 | 0 | 0 |  |  | Active (idle) | Active (low) | Active (full)
52 | Ethernet port | 0 | 0 | 0 | 0 | 0
53 | SFP port | 0 | 0 | 0 | 0 | 0 |  | W | 0 | 0 | 0
54 | Max. charging current |  |  |  | 567.3913 | 0
55 | PRA-SCx | 0 | 0 | 0 | 0 | 0 |  | BTU/h | 0 | 0 | 0
56 | Ethernet port | 0 | 0 | 0 | 0 | 0
57 | 3rd-Party (on 24V output) | 0 | 0 | 0 | 0 | 0 |  | kcal/h | 0 | 0 | 0
58 | PRA-AD604 | 0 | 0 | 0 | 0 | 0
59 | PRA-AD608 | 0 | 0 | 0 | 0 | 0
60 | Ethernet port total | 0 | 0 | 0 | 0 | 0
61 | PRA-ES8P2S | 0 | 0 | 0 | 0 | 0
62 | Active Ethernet ports | 0 | 0 | 0 | 0 | 0
63 | Active SFP ports | 0 | 0 | 0 | 0 | 0
64 | PoE load | 0 | 0 | 0 |  | 0
65 | 3rd-Party 1 (on 48V output) | 0 | 0 | 0 | 0 | 0
66 | 3rd-Party 2 (on 48V output) | 0 | 0 | 0 | 0 | 0
67 | 3rd-Party 3 (on 48V output) | 0 | 0 | 0 | 0 | 0
68 | MPS total: |  |  |  |  | 0 | Correction from measurements: (1.06 x calculated value) + 190
69 | PRA-CSLD / PRA-CSLW | 0 | 0 | 0 | 0 | 0
70 | PRA-CSE | 0 | 0 | 0 | 0 | 0
71 | PoE port total | 0 | 0 | 0 | 0 | 0
72 | Alarm option | 0 | 0 | 0 | 0 | 0
73 | CSLx total: |  |  |  |  | 0 | Correction from measurements: (1.06 x calculated value)
74 | PRA-ANS | 0 | 0 | 0 | 0 | 0
75 | PRA-IM16C8 | 0 | 0 | 0 | 0 | 0
76 | PRA-WCP-xx | 0 | 0 | 0 | 0 | 0
77 | Total [Ah] | 0 | 0 | 0 |  | 0
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
96
97
98
99
100
101
102
103
104
105
106
107
108
109
110
111
112
113
114
115
116
117
118
119
120
121
122
123
124
125
126
127
128
129
130
131
132
133
134
135
136
137
138
139
140
141
142
143
144
145
146
147
148
149
150
151
152
153
154
155
156
157
158
159
160
161
162
163
164
165
166
167
168
169
170
171
172
173
174
175
176
177
178
179
180
181
182
183
184
185
186
187
188
189
190
191
192
193
194
195
196
197
198
199
200
201
202
203
204
205
206
207
208
209
210
211
212
213
214
215
216
217
218
219
220
221
222
223
224
225
226
227
228
229
230
231
232
233
234
235
236
237
238
239
240
241
242
243
244
245
246
247
248
249
250
251
252
253
254
255
256
257
258
259
260
261
262
263
264
265
266
267
268
269
270
271
272
273
274
275
276
277
278
279
280
281
282
283
284
285
286
287
288
289
290
291
292
293
294
295
296
297
298
299
300
301
302
303
304
305
306
307
308
309
310
311
312
313
314
315
316
317
318
319
320
321
322
323
324
325
326
327
328
329
330
331
332
333
334
335
336
337
338
339
340
341
342
343
344
345
346
347
348
349
350
351
352
353
354
355
356
357
358
359
360
361
362
363
364
365
366
367
368
369
370
371
372
373
374
375
376
377
378
379
380
381
382
383
384
385
386
387
388
389
390
391
392
393
394
395
396
397
398
399
400
401
402
403
404
405
406
407
408
409
410
411
412
413
414
415
416
417
418
419
420
421
422
423
424
425
426
427
428
429
430
431
432
433
434
435
436
437
438
439
440
441
442
443
444
445
446
447
448
449
450
451
452
453
454
455
456
457
458
459
460
461
462
463
464
465
466
467
468
469
470
471
472
473
474
475
476
477
478
479
480
481
482
483
484
485
486
487
488
489
490
491
492
493
494
495
496
497
498
499
500
501
502
503
504
505
506
507
508
509
510
511
512
513
514
515
516
517
518
519
520
521
522
523
524
525
526
527
528
529
530
531
532
533
534
535
536
537
538
539
540
541
542
543
544
545
546
547
548
549
550
551
552
553
554
555
556
557
558
559
560
561
562
563
564
565
566
567
568
569
570
571
572
573
574
575
576
577
578
579
580
581
582
583
584
585
586
587
588
589
590
591
592
593
594
595
596
597
598
599
600
601
602
603
604
605
606
607
608
609
610
611
612
613
614
615
616
617
618
619
620
621
622
623
624
625
626
627
628
629
630
631
632
633
634
635
636
637
638
639
640
641
642
643
644
645
646
647
648
649
650
651
652
653
654
655
656
657
658
659
660
661
662
663
664
665
666
667
668
669
670
671
672
673
674
675
676
677
678
679
680
681
682
683
684
685
686
687
688
689
690
691
692
693
694
695
696
697
698
699
700
750
800
850
900
950
1000
1050
1100
1150
1200
1250
1300
1350
1400
1450
1500
1550
1600
1650
1700
1750
1800
1850
1900
1950
2000
2050
2100
2150
2200
2250
2300
2350
2400
2450
2500
2550
2600
2650
2700
2750
2800
2850
2900
2950
3000
3050
3100
3150
3200
3250
3300
3350
3400
3450
3500
3550
3600
3650
3700
3750
3800
3850
3900
3950
4000
4050
4100
4150
4200
4250
4300
4350
4400
4450
4500
4550
4600
4650
4700
4750
4800
4850
4900
4950
5000
5050
5100
5150
5200
5250
5300
5350
5400
5450
5500

## CALC_2 (hidden)
0
1 |  |  | Yellow marked cells are updated in v1.2
2 |  |  | Orange marked cells are updated in v1.3
3
4 |  | Single device battery current [mA] |  |  |  |  | All device battery current [mA] |  |  |  | Device count |  |  | Mains current [mA]
5 |  |  | Quiescent | Alarm (max) |  | Quantity |  | Quiescent | Alarm (max) |  | MPS Out 1 | MPS Out 2 | MPS Out 3 | Battery max. charging
6 | PRA-MPS3 |  | 430 | 430 |  | 0 |  | 0 | 0 |  |  |  |  | 567.3913
7 | MPS3 Ethernet port |  | 30 | 30 |  | 0 |  | 0 | 0
8 | MPS3 SFP port |  | 60 | 60 |  | 0 |  | 0 | 0
9
10 | PRA-SCx |  | 350 | 350 |  | 0 |  | 0 | 0
11 | SCx Ethernet port |  | 40 | 40 |  | 0 |  | 0 | 0
12
13 | 3rd-Party (on 24V output) |  | 0 | 0 |  | 0 |  | 0 | 0
14 | [13 empty] | Max. current [mA]
15 | PRA-AD604 |  | 670 |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 1060.6957
16 | Amp. Ethernet ports |  | 30 | 30 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0
17 | Total LSP load |  |  |  |  | 0 |  |  |  |  | 0 | 0 | 0
18 | PRA-AD608 |  | 790 |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 1178.087
19 | Amp. Ethernet ports |  | 30 | 30 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0
20 | Total LSP load |  |  |  |  | 0 |  |  |  |  | 0 | 0 | 0
21 | PRA-ES8P2S |  | 700 | 700 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0
22 | Active Ethernet ports |  | 40 | 40 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0
23 | Active SFP ports |  | 70 | 70 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0
24 | PoE load |  |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0
25 | 3rd-Party 1 (on 48V output) |  | 0 | 0 |  | 0 |  | 0 | 0
26 | 3rd-Party 2 (on 48V output) |  | 0 | 0 |  | 0 |  | 0 | 0
27 | 3rd-Party 3 (on 48V output) |  | 0 | 0 |  | 0 |  | 0 | 0
28
29 | PRA-CSLD |  | 420 | 420 |  | 0 |  | 0 | 0
30 | PRA-CSLW |  | 420 | 420 |  | 0 |  | 0 | 0
31 | PRA-CSE |  | 10 | 10 |  | 0 |  | 0 | 0 |  |  | 0 | PoE port(s) minimal required
32 | CS PoE port |  | 50 | 50 |  | 0 |  | 0 | 0 |  |  | 0 | PoE port(s) available without ANS
33 | CS Alarm option |  | 120 | 120 |  | 0 |  | 0 | 0
34
35 | PRA-ANS |  | 158 | 158 |  | 0 |  | 0 | 0 |  |  | 0 | PoE port(s) available with ANS
36
37 | PRA-IM16C8 |  | 370 | 370 |  | 0 |  | 0 | 0 |  |  | 0 | PoE port(s) available with IM16C8
38
39 | PRA-WCP-xx |  | 130 | 130 |  | 0 |  | 0 | 0 |  |  | 0 | PoE port(s) available with WCP-xx
40
41 | [5 empty] | 0 |  | 0 | 0
42 |  |  |  |  | Without MPS: | 0 |  | 0 | 0
43
44 |  |  | Selected quantity check |  |  | 0
45 |  |  |  | Quantity check MPS |  | FALSE
46 |  |  |  | Quantity check CSLx |  | FALSE
47
48
49 | Device | Battery capacity [Ah] |  | Total [Ah] | Mains current [mA] |  |  | Total heat loss
50 |  | Quiescent | Alarm |  | Single | Total
51 | PRA-MPS3 | 0 | 0 | 0 | 0 | 0 |  |  | Active (idle) | Active (low) | Active (full)
52 | Ethernet port | 0 | 0 | 0 | 0 | 0
53 | SFP port | 0 | 0 | 0 | 0 | 0 |  | W | 0 | 0 | 0
54 | Max. charging current |  |  |  | 567.3913 | 0
55 | PRA-SCx | 0 | 0 | 0 | 0 | 0 |  | BTU/h | 0 | 0 | 0
56 | Ethernet port | 0 | 0 | 0 | 0 | 0
57 | 3rd-Party (on 24V output) | 0 | 0 | 0 | 0 | 0 |  | kcal/h | 0 | 0 | 0
58 | PRA-AD604 | 0 | 0 | 0 | 0 | 0
59 | PRA-AD608 | 0 | 0 | 0 | 0 | 0
60 | Ethernet port total | 0 | 0 | 0 | 0 | 0
61 | PRA-ES8P2S | 0 | 0 | 0 | 0 | 0
62 | Active Ethernet ports | 0 | 0 | 0 | 0 | 0
63 | Active SFP ports | 0 | 0 | 0 | 0 | 0
64 | PoE load | 0 | 0 | 0 |  | 0
65 | 3rd-Party 1 (on 48V output) | 0 | 0 | 0 | 0 | 0
66 | 3rd-Party 2 (on 48V output) | 0 | 0 | 0 | 0 | 0
67 | 3rd-Party 3 (on 48V output) | 0 | 0 | 0 | 0 | 0
68 | MPS total: |  |  |  |  | 0 | Correction from measurements: (1.06 x calculated value) + 190
69 | PRA-CSLD / PRA-CSLW | 0 | 0 | 0 | 0 | 0
70 | PRA-CSE | 0 | 0 | 0 | 0 | 0
71 | PoE port total | 0 | 0 | 0 | 0 | 0
72 | Alarm option | 0 | 0 | 0 | 0 | 0
73 | CSLx total: |  |  |  |  | 0 | Correction from measurements: (1.06 x calculated value)
74 | PRA-ANS | 0 | 0 | 0 | 0 | 0
75 | PRA-IM16C8 | 0 | 0 | 0 | 0 | 0
76 | PRA-WCP-xx | 0 | 0 | 0 | 0 | 0
77 | Total [Ah] | 0 | 0 | 0 |  | 0
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
96
97
98
99
100
101
102
103
104
105
106
107
108
109
110
111
112
113
114
115
116
117
118
119
120
121
122
123
124
125
126
127
128
129
130
131
132
133
134
135
136
137
138
139
140
141
142
143
144
145
146
147
148
149
150
151
152
153
154
155
156
157
158
159
160
161
162
163
164
165
166
167
168
169
170
171
172
173
174
175
176
177
178
179
180
181
182
183
184
185
186
187
188
189
190
191
192
193
194
195
196
197
198
199
200
201
202
203
204
205
206
207
208
209
210
211
212
213
214
215
216
217
218
219
220
221
222
223
224
225
226
227
228
229
230
231
232
233
234
235
236
237
238
239
240
241
242
243
244
245
246
247
248
249
250
251
252
253
254
255
256
257
258
259
260
261
262
263
264
265
266
267
268
269
270
271
272
273
274
275
276
277
278
279
280
281
282
283
284
285
286
287
288
289
290
291
292
293
294
295
296
297
298
299
300
301
302
303
304
305
306
307
308
309
310
311
312
313
314
315
316
317
318
319
320
321
322
323
324
325
326
327
328
329
330
331
332
333
334
335
336
337
338
339
340
341
342
343
344
345
346
347
348
349
350
351
352
353
354
355
356
357
358
359
360
361
362
363
364
365
366
367
368
369
370
371
372
373
374
375
376
377
378
379
380
381
382
383
384
385
386
387
388
389
390
391
392
393
394
395
396
397
398
399
400
401
402
403
404
405
406
407
408
409
410
411
412
413
414
415
416
417
418
419
420
421
422
423
424
425
426
427
428
429
430
431
432
433
434
435
436
437
438
439
440
441
442
443
444
445
446
447
448
449
450
451
452
453
454
455
456
457
458
459
460
461
462
463
464
465
466
467
468
469
470
471
472
473
474
475
476
477
478
479
480
481
482
483
484
485
486
487
488
489
490
491
492
493
494
495
496
497
498
499
500
501
502
503
504
505
506
507
508
509
510
511
512
513
514
515
516
517
518
519
520
521
522
523
524
525
526
527
528
529
530
531
532
533
534
535
536
537
538
539
540
541
542
543
544
545
546
547
548
549
550
551
552
553
554
555
556
557
558
559
560
561
562
563
564
565
566
567
568
569
570
571
572
573
574
575
576
577
578
579
580
581
582
583
584
585
586
587
588
589
590
591
592
593
594
595
596
597
598
599
600
601
602
603
604
605
606
607
608
609
610
611
612
613
614
615
616
617
618
619
620
621
622
623
624
625
626
627
628
629
630
631
632
633
634
635
636
637
638
639
640
641
642
643
644
645
646
647
648
649
650
651
652
653
654
655
656
657
658
659
660
661
662
663
664
665
666
667
668
669
670
671
672
673
674
675
676
677
678
679
680
681
682
683
684
685
686
687
688
689
690
691
692
693
694
695
696
697
698
699
700
750
800
850
900
950
1000
1050
1100
1150
1200
1250
1300
1350
1400
1450
1500
1550
1600
1650
1700
1750
1800
1850
1900
1950
2000
2050
2100
2150
2200
2250
2300
2350
2400
2450
2500
2550
2600
2650
2700
2750
2800
2850
2900
2950
3000
3050
3100
3150
3200
3250
3300
3350
3400
3450
3500
3550
3600
3650
3700
3750
3800
3850
3900
3950
4000
4050
4100
4150
4200
4250
4300
4350
4400
4450
4500
4550
4600
4650
4700
4750
4800
4850
4900
4950
5000
5050
5100
5150
5200
5250
5300
5350
5400
5450
5500

## CALC_3 (hidden)
0
1 |  |  | Yellow marked cells are updated in v1.2
2 |  |  | Orange marked cells are updated in v1.3
3
4 |  | Single device battery current [mA] |  |  |  |  | All device battery current [mA] |  |  |  | Device count |  |  | Mains current [mA]
5 |  |  | Quiescent | Alarm (max) |  | Quantity |  | Quiescent | Alarm (max) |  | MPS Out 1 | MPS Out 2 | MPS Out 3 | Battery max. charging
6 | PRA-MPS3 |  | 430 | 430 |  | 0 |  | 0 | 0 |  |  |  |  | 567.3913
7 | MPS3 Ethernet port |  | 30 | 30 |  | 0 |  | 0 | 0
8 | MPS3 SFP port |  | 60 | 60 |  | 0 |  | 0 | 0
9
10 | PRA-SCx |  | 350 | 350 |  | 0 |  | 0 | 0
11 | SCx Ethernet port |  | 40 | 40 |  | 0 |  | 0 | 0
12
13 | 3rd-Party (on 24V output) |  | 0 | 0 |  | 0 |  | 0 | 0
14 | [13 empty] | Max. current [mA]
15 | PRA-AD604 |  | 670 |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 1060.6957
16 | Amp. Ethernet ports |  | 30 | 30 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0
17 | Total LSP load |  |  |  |  | 0 |  |  |  |  | 0 | 0 | 0
18 | PRA-AD608 |  | 790 |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 1178.087
19 | Amp. Ethernet ports |  | 30 | 30 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0
20 | Total LSP load |  |  |  |  | 0 |  |  |  |  | 0 | 0 | 0
21 | PRA-ES8P2S |  | 700 | 700 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0
22 | Active Ethernet ports |  | 40 | 40 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0
23 | Active SFP ports |  | 70 | 70 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0
24 | PoE load |  |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0
25 | 3rd-Party 1 (on 48V output) |  | 0 | 0 |  | 0 |  | 0 | 0
26 | 3rd-Party 2 (on 48V output) |  | 0 | 0 |  | 0 |  | 0 | 0
27 | 3rd-Party 3 (on 48V output) |  | 0 | 0 |  | 0 |  | 0 | 0
28
29 | PRA-CSLD |  | 420 | 420 |  | 0 |  | 0 | 0
30 | PRA-CSLW |  | 420 | 420 |  | 0 |  | 0 | 0
31 | PRA-CSE |  | 10 | 10 |  | 0 |  | 0 | 0 |  |  | 0 | PoE port(s) minimal required
32 | CS PoE port |  | 50 | 50 |  | 0 |  | 0 | 0 |  |  | 0 | PoE port(s) available without ANS
33 | CS Alarm option |  | 120 | 120 |  | 0 |  | 0 | 0
34
35 | PRA-ANS |  | 158 | 158 |  | 0 |  | 0 | 0 |  |  | 0 | PoE port(s) available with ANS
36
37 | PRA-IM16C8 |  | 370 | 370 |  | 0 |  | 0 | 0 |  |  | 0 | PoE port(s) available with IM16C8
38
39 | PRA-WCP-xx |  | 130 | 130 |  | 0 |  | 0 | 0 |  |  | 0 | PoE port(s) available with WCP-xx
40
41 | [5 empty] | 0 |  | 0 | 0
42 |  |  |  |  | Without MPS: | 0 |  | 0 | 0
43
44 |  |  | Selected quantity check |  |  | 0
45 |  |  |  | Quantity check MPS |  | FALSE
46 |  |  |  | Quantity check CSLx |  | FALSE
47
48
49 | Device | Battery capacity [Ah] |  | Total [Ah] | Mains current [mA] |  |  | Total heat loss
50 |  | Quiescent | Alarm |  | Single | Total
51 | PRA-MPS3 | 0 | 0 | 0 | 0 | 0 |  |  | Active (idle) | Active (low) | Active (full)
52 | Ethernet port | 0 | 0 | 0 | 0 | 0
53 | SFP port | 0 | 0 | 0 | 0 | 0 |  | W | 0 | 0 | 0
54 | Max. charging current |  |  |  | 567.3913 | 0
55 | PRA-SCx | 0 | 0 | 0 | 0 | 0 |  | BTU/h | 0 | 0 | 0
56 | Ethernet port | 0 | 0 | 0 | 0 | 0
57 | 3rd-Party (on 24V output) | 0 | 0 | 0 | 0 | 0 |  | kcal/h | 0 | 0 | 0
58 | PRA-AD604 | 0 | 0 | 0 | 0 | 0
59 | PRA-AD608 | 0 | 0 | 0 | 0 | 0
60 | Ethernet port total | 0 | 0 | 0 | 0 | 0
61 | PRA-ES8P2S | 0 | 0 | 0 | 0 | 0
62 | Active Ethernet ports | 0 | 0 | 0 | 0 | 0
63 | Active SFP ports | 0 | 0 | 0 | 0 | 0
64 | PoE load | 0 | 0 | 0 |  | 0
65 | 3rd-Party 1 (on 48V output) | 0 | 0 | 0 | 0 | 0
66 | 3rd-Party 2 (on 48V output) | 0 | 0 | 0 | 0 | 0
67 | 3rd-Party 3 (on 48V output) | 0 | 0 | 0 | 0 | 0
68 | MPS total: |  |  |  |  | 0 | Correction from measurements: (1.06 x calculated value) + 190
69 | PRA-CSLD / PRA-CSLW | 0 | 0 | 0 | 0 | 0
70 | PRA-CSE | 0 | 0 | 0 | 0 | 0
71 | PoE port total | 0 | 0 | 0 | 0 | 0
72 | Alarm option | 0 | 0 | 0 | 0 | 0
73 | CSLx total: |  |  |  |  | 0 | Correction from measurements: (1.06 x calculated value)
74 | PRA-ANS | 0 | 0 | 0 | 0 | 0
75 | PRA-IM16C8 | 0 | 0 | 0 | 0 | 0
76 | PRA-WCP-xx | 0 | 0 | 0 | 0 | 0
77 | Total [Ah] | 0 | 0 | 0 |  | 0
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
96
97
98
99
100
101
102
103
104
105
106
107
108
109
110
111
112
113
114
115
116
117
118
119
120
121
122
123
124
125
126
127
128
129
130
131
132
133
134
135
136
137
138
139
140
141
142
143
144
145
146
147
148
149
150
151
152
153
154
155
156
157
158
159
160
161
162
163
164
165
166
167
168
169
170
171
172
173
174
175
176
177
178
179
180
181
182
183
184
185
186
187
188
189
190
191
192
193
194
195
196
197
198
199
200
201
202
203
204
205
206
207
208
209
210
211
212
213
214
215
216
217
218
219
220
221
222
223
224
225
226
227
228
229
230
231
232
233
234
235
236
237
238
239
240
241
242
243
244
245
246
247
248
249
250
251
252
253
254
255
256
257
258
259
260
261
262
263
264
265
266
267
268
269
270
271
272
273
274
275
276
277
278
279
280
281
282
283
284
285
286
287
288
289
290
291
292
293
294
295
296
297
298
299
300
301
302
303
304
305
306
307
308
309
310
311
312
313
314
315
316
317
318
319
320
321
322
323
324
325
326
327
328
329
330
331
332
333
334
335
336
337
338
339
340
341
342
343
344
345
346
347
348
349
350
351
352
353
354
355
356
357
358
359
360
361
362
363
364
365
366
367
368
369
370
371
372
373
374
375
376
377
378
379
380
381
382
383
384
385
386
387
388
389
390
391
392
393
394
395
396
397
398
399
400
401
402
403
404
405
406
407
408
409
410
411
412
413
414
415
416
417
418
419
420
421
422
423
424
425
426
427
428
429
430
431
432
433
434
435
436
437
438
439
440
441
442
443
444
445
446
447
448
449
450
451
452
453
454
455
456
457
458
459
460
461
462
463
464
465
466
467
468
469
470
471
472
473
474
475
476
477
478
479
480
481
482
483
484
485
486
487
488
489
490
491
492
493
494
495
496
497
498
499
500
501
502
503
504
505
506
507
508
509
510
511
512
513
514
515
516
517
518
519
520
521
522
523
524
525
526
527
528
529
530
531
532
533
534
535
536
537
538
539
540
541
542
543
544
545
546
547
548
549
550
551
552
553
554
555
556
557
558
559
560
561
562
563
564
565
566
567
568
569
570
571
572
573
574
575
576
577
578
579
580
581
582
583
584
585
586
587
588
589
590
591
592
593
594
595
596
597
598
599
600
601
602
603
604
605
606
607
608
609
610
611
612
613
614
615
616
617
618
619
620
621
622
623
624
625
626
627
628
629
630
631
632
633
634
635
636
637
638
639
640
641
642
643
644
645
646
647
648
649
650
651
652
653
654
655
656
657
658
659
660
661
662
663
664
665
666
667
668
669
670
671
672
673
674
675
676
677
678
679
680
681
682
683
684
685
686
687
688
689
690
691
692
693
694
695
696
697
698
699
700
750
800
850
900
950
1000
1050
1100
1150
1200
1250
1300
1350
1400
1450
1500
1550
1600
1650
1700
1750
1800
1850
1900
1950
2000
2050
2100
2150
2200
2250
2300
2350
2400
2450
2500
2550
2600
2650
2700
2750
2800
2850
2900
2950
3000
3050
3100
3150
3200
3250
3300
3350
3400
3450
3500
3550
3600
3650
3700
3750
3800
3850
3900
3950
4000
4050
4100
4150
4200
4250
4300
4350
4400
4450
4500
4550
4600
4650
4700
4750
4800
4850
4900
4950
5000
5050
5100
5150
5200
5250
5300
5350
5400
5450
5500

## CALC_4 (hidden)
0
1 |  |  | Yellow marked cells are updated in v1.2
2 |  |  | Orange marked cells are updated in v1.3
3
4 |  | Single device battery current [mA] |  |  |  |  | All device battery current [mA] |  |  |  | Device count |  |  | Mains current [mA]
5 |  |  | Quiescent | Alarm (max) |  | Quantity |  | Quiescent | Alarm (max) |  | MPS Out 1 | MPS Out 2 | MPS Out 3 | Battery max. charging
6 | PRA-MPS3 |  | 430 | 430 |  | 0 |  | 0 | 0 |  |  |  |  | 567.3913
7 | MPS3 Ethernet port |  | 30 | 30 |  | 0 |  | 0 | 0
8 | MPS3 SFP port |  | 60 | 60 |  | 0 |  | 0 | 0
9
10 | PRA-SCx |  | 350 | 350 |  | 0 |  | 0 | 0
11 | SCx Ethernet port |  | 40 | 40 |  | 0 |  | 0 | 0
12
13 | 3rd-Party (on 24V output) |  | 0 | 0 |  | 0 |  | 0 | 0
14 | [13 empty] | Max. current [mA]
15 | PRA-AD604 |  | 670 |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 1060.6957
16 | Amp. Ethernet ports |  | 30 | 30 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0
17 | Total LSP load |  |  |  |  | 0 |  |  |  |  | 0 | 0 | 0
18 | PRA-AD608 |  | 790 |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 1178.087
19 | Amp. Ethernet ports |  | 30 | 30 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0
20 | Total LSP load |  |  |  |  | 0 |  |  |  |  | 0 | 0 | 0
21 | PRA-ES8P2S |  | 700 | 700 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0
22 | Active Ethernet ports |  | 40 | 40 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0
23 | Active SFP ports |  | 70 | 70 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0
24 | PoE load |  |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0
25 | 3rd-Party 1 (on 48V output) |  | 0 | 0 |  | 0 |  | 0 | 0
26 | 3rd-Party 2 (on 48V output) |  | 0 | 0 |  | 0 |  | 0 | 0
27 | 3rd-Party 3 (on 48V output) |  | 0 | 0 |  | 0 |  | 0 | 0
28
29 | PRA-CSLD |  | 420 | 420 |  | 0 |  | 0 | 0
30 | PRA-CSLW |  | 420 | 420 |  | 0 |  | 0 | 0
31 | PRA-CSE |  | 10 | 10 |  | 0 |  | 0 | 0 |  |  | 0 | PoE port(s) minimal required
32 | CS PoE port |  | 50 | 50 |  | 0 |  | 0 | 0 |  |  | 0 | PoE port(s) available without ANS
33 | CS Alarm option |  | 120 | 120 |  | 0 |  | 0 | 0
34
35 | PRA-ANS |  | 158 | 158 |  | 0 |  | 0 | 0 |  |  | 0 | PoE port(s) available with ANS
36
37 | PRA-IM16C8 |  | 370 | 370 |  | 0 |  | 0 | 0 |  |  | 0 | PoE port(s) available with IM16C8
38
39 | PRA-WCP-xx |  | 130 | 130 |  | 0 |  | 0 | 0 |  |  | 0 | PoE port(s) available with WCP-xx
40
41 | [5 empty] | 0 |  | 0 | 0
42 |  |  |  |  | Without MPS: | 0 |  | 0 | 0
43
44 |  |  | Selected quantity check |  |  | 0
45 |  |  |  | Quantity check MPS |  | FALSE
46 |  |  |  | Quantity check CSLx |  | FALSE
47
48
49 | Device | Battery capacity [Ah] |  | Total [Ah] | Mains current [mA] |  |  | Total heat loss
50 |  | Quiescent | Alarm |  | Single | Total
51 | PRA-MPS3 | 0 | 0 | 0 | 0 | 0 |  |  | Active (idle) | Active (low) | Active (full)
52 | Ethernet port | 0 | 0 | 0 | 0 | 0
53 | SFP port | 0 | 0 | 0 | 0 | 0 |  | W | 0 | 0 | 0
54 | Max. charging current |  |  |  | 567.3913 | 0
55 | PRA-SCx | 0 | 0 | 0 | 0 | 0 |  | BTU/h | 0 | 0 | 0
56 | Ethernet port | 0 | 0 | 0 | 0 | 0
57 | 3rd-Party (on 24V output) | 0 | 0 | 0 | 0 | 0 |  | kcal/h | 0 | 0 | 0
58 | PRA-AD604 | 0 | 0 | 0 | 0 | 0
59 | PRA-AD608 | 0 | 0 | 0 | 0 | 0
60 | Ethernet port total | 0 | 0 | 0 | 0 | 0
61 | PRA-ES8P2S | 0 | 0 | 0 | 0 | 0
62 | Active Ethernet ports | 0 | 0 | 0 | 0 | 0
63 | Active SFP ports | 0 | 0 | 0 | 0 | 0
64 | PoE load | 0 | 0 | 0 |  | 0
65 | 3rd-Party 1 (on 48V output) | 0 | 0 | 0 | 0 | 0
66 | 3rd-Party 2 (on 48V output) | 0 | 0 | 0 | 0 | 0
67 | 3rd-Party 3 (on 48V output) | 0 | 0 | 0 | 0 | 0
68 | MPS total: |  |  |  |  | 0 | Correction from measurements: (1.06 x calculated value) + 190
69 | PRA-CSLD / PRA-CSLW | 0 | 0 | 0 | 0 | 0
70 | PRA-CSE | 0 | 0 | 0 | 0 | 0
71 | PoE port total | 0 | 0 | 0 | 0 | 0
72 | Alarm option | 0 | 0 | 0 | 0 | 0
73 | CSLx total: |  |  |  |  | 0 | Correction from measurements: (1.06 x calculated value)
74 | PRA-ANS | 0 | 0 | 0 | 0 | 0
75 | PRA-IM16C8 | 0 | 0 | 0 | 0 | 0
76 | PRA-WCP-xx | 0 | 0 | 0 | 0 | 0
77 | Total [Ah] | 0 | 0 | 0 |  | 0
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
96
97
98
99
100
101
102
103
104
105
106
107
108
109
110
111
112
113
114
115
116
117
118
119
120
121
122
123
124
125
126
127
128
129
130
131
132
133
134
135
136
137
138
139
140
141
142
143
144
145
146
147
148
149
150
151
152
153
154
155
156
157
158
159
160
161
162
163
164
165
166
167
168
169
170
171
172
173
174
175
176
177
178
179
180
181
182
183
184
185
186
187
188
189
190
191
192
193
194
195
196
197
198
199
200
201
202
203
204
205
206
207
208
209
210
211
212
213
214
215
216
217
218
219
220
221
222
223
224
225
226
227
228
229
230
231
232
233
234
235
236
237
238
239
240
241
242
243
244
245
246
247
248
249
250
251
252
253
254
255
256
257
258
259
260
261
262
263
264
265
266
267
268
269
270
271
272
273
274
275
276
277
278
279
280
281
282
283
284
285
286
287
288
289
290
291
292
293
294
295
296
297
298
299
300
301
302
303
304
305
306
307
308
309
310
311
312
313
314
315
316
317
318
319
320
321
322
323
324
325
326
327
328
329
330
331
332
333
334
335
336
337
338
339
340
341
342
343
344
345
346
347
348
349
350
351
352
353
354
355
356
357
358
359
360
361
362
363
364
365
366
367
368
369
370
371
372
373
374
375
376
377
378
379
380
381
382
383
384
385
386
387
388
389
390
391
392
393
394
395
396
397
398
399
400
401
402
403
404
405
406
407
408
409
410
411
412
413
414
415
416
417
418
419
420
421
422
423
424
425
426
427
428
429
430
431
432
433
434
435
436
437
438
439
440
441
442
443
444
445
446
447
448
449
450
451
452
453
454
455
456
457
458
459
460
461
462
463
464
465
466
467
468
469
470
471
472
473
474
475
476
477
478
479
480
481
482
483
484
485
486
487
488
489
490
491
492
493
494
495
496
497
498
499
500
501
502
503
504
505
506
507
508
509
510
511
512
513
514
515
516
517
518
519
520
521
522
523
524
525
526
527
528
529
530
531
532
533
534
535
536
537
538
539
540
541
542
543
544
545
546
547
548
549
550
551
552
553
554
555
556
557
558
559
560
561
562
563
564
565
566
567
568
569
570
571
572
573
574
575
576
577
578
579
580
581
582
583
584
585
586
587
588
589
590
591
592
593
594
595
596
597
598
599
600
601
602
603
604
605
606
607
608
609
610
611
612
613
614
615
616
617
618
619
620
621
622
623
624
625
626
627
628
629
630
631
632
633
634
635
636
637
638
639
640
641
642
643
644
645
646
647
648
649
650
651
652
653
654
655
656
657
658
659
660
661
662
663
664
665
666
667
668
669
670
671
672
673
674
675
676
677
678
679
680
681
682
683
684
685
686
687
688
689
690
691
692
693
694
695
696
697
698
699
700
750
800
850
900
950
1000
1050
1100
1150
1200
1250
1300
1350
1400
1450
1500
1550
1600
1650
1700
1750
1800
1850
1900
1950
2000
2050
2100
2150
2200
2250
2300
2350
2400
2450
2500
2550
2600
2650
2700
2750
2800
2850
2900
2950
3000
3050
3100
3150
3200
3250
3300
3350
3400
3450
3500
3550
3600
3650
3700
3750
3800
3850
3900
3950
4000
4050
4100
4150
4200
4250
4300
4350
4400
4450
4500
4550
4600
4650
4700
4750
4800
4850
4900
4950
5000
5050
5100
5150
5200
5250
5300
5350
5400
5450
5500

## CALC_5 (hidden)
0
1 |  |  | Yellow marked cells are updated in v1.2
2 |  |  | Orange marked cells are updated in v1.3
3
4 |  | Single device battery current [mA] |  |  |  |  | All device battery current [mA] |  |  |  | Device count |  |  | Mains current [mA]
5 |  |  | Quiescent | Alarm (max) |  | Quantity |  | Quiescent | Alarm (max) |  | MPS Out 1 | MPS Out 2 | MPS Out 3 | Battery max. charging
6 | PRA-MPS3 |  | 430 | 430 |  | 0 |  | 0 | 0 |  |  |  |  | 567.3913
7 | MPS3 Ethernet port |  | 30 | 30 |  | 0 |  | 0 | 0
8 | MPS3 SFP port |  | 60 | 60 |  | 0 |  | 0 | 0
9
10 | PRA-SCx |  | 350 | 350 |  | 0 |  | 0 | 0
11 | SCx Ethernet port |  | 40 | 40 |  | 0 |  | 0 | 0
12
13 | 3rd-Party (on 24V output) |  | 0 | 0 |  | 0 |  | 0 | 0
14 | [13 empty] | Max. current [mA]
15 | PRA-AD604 |  | 670 |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 1060.6957
16 | Amp. Ethernet ports |  | 30 | 30 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0
17 | Total LSP load |  |  |  |  | 0 |  |  |  |  | 0 | 0 | 0
18 | PRA-AD608 |  | 790 |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 1178.087
19 | Amp. Ethernet ports |  | 30 | 30 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0
20 | Total LSP load |  |  |  |  | 0 |  |  |  |  | 0 | 0 | 0
21 | PRA-ES8P2S |  | 700 | 700 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0
22 | Active Ethernet ports |  | 40 | 40 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0
23 | Active SFP ports |  | 70 | 70 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0
24 | PoE load |  |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0
25 | 3rd-Party 1 (on 48V output) |  | 0 | 0 |  | 0 |  | 0 | 0
26 | 3rd-Party 2 (on 48V output) |  | 0 | 0 |  | 0 |  | 0 | 0
27 | 3rd-Party 3 (on 48V output) |  | 0 | 0 |  | 0 |  | 0 | 0
28
29 | PRA-CSLD |  | 420 | 420 |  | 0 |  | 0 | 0
30 | PRA-CSLW |  | 420 | 420 |  | 0 |  | 0 | 0
31 | PRA-CSE |  | 10 | 10 |  | 0 |  | 0 | 0 |  |  | 0 | PoE port(s) minimal required
32 | CS PoE port |  | 50 | 50 |  | 0 |  | 0 | 0 |  |  | 0 | PoE port(s) available without ANS
33 | CS Alarm option |  | 120 | 120 |  | 0 |  | 0 | 0
34
35 | PRA-ANS |  | 158 | 158 |  | 0 |  | 0 | 0 |  |  | 0 | PoE port(s) available with ANS
36
37 | PRA-IM16C8 |  | 370 | 370 |  | 0 |  | 0 | 0 |  |  | 0 | PoE port(s) available with IM16C8
38
39 | PRA-WCP-xx |  | 130 | 130 |  | 0 |  | 0 | 0 |  |  | 0 | PoE port(s) available with WCP-xx
40
41 | [5 empty] | 0 |  | 0 | 0
42 |  |  |  |  | Without MPS: | 0 |  | 0 | 0
43
44 |  |  | Selected quantity check |  |  | 0
45 |  |  |  | Quantity check MPS |  | FALSE
46 |  |  |  | Quantity check CSLx |  | FALSE
47
48
49 | Device | Battery capacity [Ah] |  | Total [Ah] | Mains current [mA] |  |  | Total heat loss
50 |  | Quiescent | Alarm |  | Single | Total
51 | PRA-MPS3 | 0 | 0 | 0 | 0 | 0 |  |  | Active (idle) | Active (low) | Active (full)
52 | Ethernet port | 0 | 0 | 0 | 0 | 0
53 | SFP port | 0 | 0 | 0 | 0 | 0 |  | W | 0 | 0 | 0
54 | Max. charging current |  |  |  | 567.3913 | 0
55 | PRA-SCx | 0 | 0 | 0 | 0 | 0 |  | BTU/h | 0 | 0 | 0
56 | Ethernet port | 0 | 0 | 0 | 0 | 0
57 | 3rd-Party (on 24V output) | 0 | 0 | 0 | 0 | 0 |  | kcal/h | 0 | 0 | 0
58 | PRA-AD604 | 0 | 0 | 0 | 0 | 0
59 | PRA-AD608 | 0 | 0 | 0 | 0 | 0
60 | Ethernet port total | 0 | 0 | 0 | 0 | 0
61 | PRA-ES8P2S | 0 | 0 | 0 | 0 | 0
62 | Active Ethernet ports | 0 | 0 | 0 | 0 | 0
63 | Active SFP ports | 0 | 0 | 0 | 0 | 0
64 | PoE load | 0 | 0 | 0 |  | 0
65 | 3rd-Party 1 (on 48V output) | 0 | 0 | 0 | 0 | 0
66 | 3rd-Party 2 (on 48V output) | 0 | 0 | 0 | 0 | 0
67 | 3rd-Party 3 (on 48V output) | 0 | 0 | 0 | 0 | 0
68 | MPS total: |  |  |  |  | 0 | Correction from measurements: (1.06 x calculated value) + 190
69 | PRA-CSLD / PRA-CSLW | 0 | 0 | 0 | 0 | 0
70 | PRA-CSE | 0 | 0 | 0 | 0 | 0
71 | PoE port total | 0 | 0 | 0 | 0 | 0
72 | Alarm option | 0 | 0 | 0 | 0 | 0
73 | CSLx total: |  |  |  |  | 0 | Correction from measurements: (1.06 x calculated value)
74 | PRA-ANS | 0 | 0 | 0 | 0 | 0
75 | PRA-IM16C8 | 0 | 0 | 0 | 0 | 0
76 | PRA-WCP-xx | 0 | 0 | 0 | 0 | 0
77 | Total [Ah] | 0 | 0 | 0 |  | 0
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
96
97
98
99
100
101
102
103
104
105
106
107
108
109
110
111
112
113
114
115
116
117
118
119
120
121
122
123
124
125
126
127
128
129
130
131
132
133
134
135
136
137
138
139
140
141
142
143
144
145
146
147
148
149
150
151
152
153
154
155
156
157
158
159
160
161
162
163
164
165
166
167
168
169
170
171
172
173
174
175
176
177
178
179
180
181
182
183
184
185
186
187
188
189
190
191
192
193
194
195
196
197
198
199
200
201
202
203
204
205
206
207
208
209
210
211
212
213
214
215
216
217
218
219
220
221
222
223
224
225
226
227
228
229
230
231
232
233
234
235
236
237
238
239
240
241
242
243
244
245
246
247
248
249
250
251
252
253
254
255
256
257
258
259
260
261
262
263
264
265
266
267
268
269
270
271
272
273
274
275
276
277
278
279
280
281
282
283
284
285
286
287
288
289
290
291
292
293
294
295
296
297
298
299
300
301
302
303
304
305
306
307
308
309
310
311
312
313
314
315
316
317
318
319
320
321
322
323
324
325
326
327
328
329
330
331
332
333
334
335
336
337
338
339
340
341
342
343
344
345
346
347
348
349
350
351
352
353
354
355
356
357
358
359
360
361
362
363
364
365
366
367
368
369
370
371
372
373
374
375
376
377
378
379
380
381
382
383
384
385
386
387
388
389
390
391
392
393
394
395
396
397
398
399
400
401
402
403
404
405
406
407
408
409
410
411
412
413
414
415
416
417
418
419
420
421
422
423
424
425
426
427
428
429
430
431
432
433
434
435
436
437
438
439
440
441
442
443
444
445
446
447
448
449
450
451
452
453
454
455
456
457
458
459
460
461
462
463
464
465
466
467
468
469
470
471
472
473
474
475
476
477
478
479
480
481
482
483
484
485
486
487
488
489
490
491
492
493
494
495
496
497
498
499
500
501
502
503
504
505
506
507
508
509
510
511
512
513
514
515
516
517
518
519
520
521
522
523
524
525
526
527
528
529
530
531
532
533
534
535
536
537
538
539
540
541
542
543
544
545
546
547
548
549
550
551
552
553
554
555
556
557
558
559
560
561
562
563
564
565
566
567
568
569
570
571
572
573
574
575
576
577
578
579
580
581
582
583
584
585
586
587
588
589
590
591
592
593
594
595
596
597
598
599
600
601
602
603
604
605
606
607
608
609
610
611
612
613
614
615
616
617
618
619
620
621
622
623
624
625
626
627
628
629
630
631
632
633
634
635
636
637
638
639
640
641
642
643
644
645
646
647
648
649
650
651
652
653
654
655
656
657
658
659
660
661
662
663
664
665
666
667
668
669
670
671
672
673
674
675
676
677
678
679
680
681
682
683
684
685
686
687
688
689
690
691
692
693
694
695
696
697
698
699
700
750
800
850
900
950
1000
1050
1100
1150
1200
1250
1300
1350
1400
1450
1500
1550
1600
1650
1700
1750
1800
1850
1900
1950
2000
2050
2100
2150
2200
2250
2300
2350
2400
2450
2500
2550
2600
2650
2700
2750
2800
2850
2900
2950
3000
3050
3100
3150
3200
3250
3300
3350
3400
3450
3500
3550
3600
3650
3700
3750
3800
3850
3900
3950
4000
4050
4100
4150
4200
4250
4300
4350
4400
4450
4500
4550
4600
4650
4700
4750
4800
4850
4900
4950
5000
5050
5100
5150
5200
5250
5300
5350
5400
5450
5500

## CALC_6 (hidden)
0
1 |  |  | Yellow marked cells are updated in v1.2
2 |  |  | Orange marked cells are updated in v1.3
3
4 |  | Single device battery current [mA] |  |  |  |  | All device battery current [mA] |  |  |  | Device count |  |  | Mains current [mA]
5 |  |  | Quiescent | Alarm (max) |  | Quantity |  | Quiescent | Alarm (max) |  | MPS Out 1 | MPS Out 2 | MPS Out 3 | Battery max. charging
6 | PRA-MPS3 |  | 430 | 430 |  | 0 |  | 0 | 0 |  |  |  |  | 567.3913
7 | MPS3 Ethernet port |  | 30 | 30 |  | 0 |  | 0 | 0
8 | MPS3 SFP port |  | 60 | 60 |  | 0 |  | 0 | 0
9
10 | PRA-SCx |  | 350 | 350 |  | 0 |  | 0 | 0
11 | SCx Ethernet port |  | 40 | 40 |  | 0 |  | 0 | 0
12
13 | 3rd-Party (on 24V output) |  | 0 | 0 |  | 0 |  | 0 | 0
14 | [13 empty] | Max. current [mA]
15 | PRA-AD604 |  | 670 |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 1060.6957
16 | Amp. Ethernet ports |  | 30 | 30 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0
17 | Total LSP load |  |  |  |  | 0 |  |  |  |  | 0 | 0 | 0
18 | PRA-AD608 |  | 790 |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 1178.087
19 | Amp. Ethernet ports |  | 30 | 30 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0
20 | Total LSP load |  |  |  |  | 0 |  |  |  |  | 0 | 0 | 0
21 | PRA-ES8P2S |  | 700 | 700 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0
22 | Active Ethernet ports |  | 40 | 40 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0
23 | Active SFP ports |  | 70 | 70 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0
24 | PoE load |  |  |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0
25 | 3rd-Party 1 (on 48V output) |  | 0 | 0 |  | 0 |  | 0 | 0
26 | 3rd-Party 2 (on 48V output) |  | 0 | 0 |  | 0 |  | 0 | 0
27 | 3rd-Party 3 (on 48V output) |  | 0 | 0 |  | 0 |  | 0 | 0
28
29 | PRA-CSLD |  | 420 | 420 |  | 0 |  | 0 | 0
30 | PRA-CSLW |  | 420 | 420 |  | 0 |  | 0 | 0
31 | PRA-CSE |  | 10 | 10 |  | 0 |  | 0 | 0 |  |  | 0 | PoE port(s) minimal required
32 | CS PoE port |  | 50 | 50 |  | 0 |  | 0 | 0 |  |  | 0 | PoE port(s) available without ANS
33 | CS Alarm option |  | 120 | 120 |  | 0 |  | 0 | 0
34
35 | PRA-ANS |  | 158 | 158 |  | 0 |  | 0 | 0 |  |  | 0 | PoE port(s) available with ANS
36
37 | PRA-IM16C8 |  | 370 | 370 |  | 0 |  | 0 | 0 |  |  | 0 | PoE port(s) available with IM16C8
38
39 | PRA-WCP-xx |  | 130 | 130 |  | 0 |  | 0 | 0 |  |  | 0 | PoE port(s) available with WCP-xx
40
41 | [5 empty] | 0 |  | 0 | 0
42 |  |  |  |  | Without MPS: | 0 |  | 0 | 0
43
44 |  |  | Selected quantity check |  |  | 0
45 |  |  |  | Quantity check MPS |  | FALSE
46 |  |  |  | Quantity check CSLx |  | FALSE
47
48
49 | Device | Battery capacity [Ah] |  | Total [Ah] | Mains current [mA] |  |  | Total heat loss
50 |  | Quiescent | Alarm |  | Single | Total
51 | PRA-MPS3 | 0 | 0 | 0 | 0 | 0 |  |  | Active (idle) | Active (low) | Active (full)
52 | Ethernet port | 0 | 0 | 0 | 0 | 0
53 | SFP port | 0 | 0 | 0 | 0 | 0 |  | W | 0 | 0 | 0
54 | Max. charging current |  |  |  | 567.3913 | 0
55 | PRA-SCx | 0 | 0 | 0 | 0 | 0 |  | BTU/h | 0 | 0 | 0
56 | Ethernet port | 0 | 0 | 0 | 0 | 0
57 | 3rd-Party (on 24V output) | 0 | 0 | 0 | 0 | 0 |  | kcal/h | 0 | 0 | 0
58 | PRA-AD604 | 0 | 0 | 0 | 0 | 0
59 | PRA-AD608 | 0 | 0 | 0 | 0 | 0
60 | Ethernet port total | 0 | 0 | 0 | 0 | 0
61 | PRA-ES8P2S | 0 | 0 | 0 | 0 | 0
62 | Active Ethernet ports | 0 | 0 | 0 | 0 | 0
63 | Active SFP ports | 0 | 0 | 0 | 0 | 0
64 | PoE load | 0 | 0 | 0 |  | 0
65 | 3rd-Party 1 (on 48V output) | 0 | 0 | 0 | 0 | 0
66 | 3rd-Party 2 (on 48V output) | 0 | 0 | 0 | 0 | 0
67 | 3rd-Party 3 (on 48V output) | 0 | 0 | 0 | 0 | 0
68 | MPS total: |  |  |  |  | 0 | Correction from measurements: (1.06 x calculated value) + 190
69 | PRA-CSLD / PRA-CSLW | 0 | 0 | 0 | 0 | 0
70 | PRA-CSE | 0 | 0 | 0 | 0 | 0
71 | PoE port total | 0 | 0 | 0 | 0 | 0
72 | Alarm option | 0 | 0 | 0 | 0 | 0
73 | CSLx total: |  |  |  |  | 0 | Correction from measurements: (1.06 x calculated value)
74 | PRA-ANS | 0 | 0 | 0 | 0 | 0
75 | PRA-IM16C8 | 0 | 0 | 0 | 0 | 0
76 | PRA-WCP-xx | 0 | 0 | 0 | 0 | 0
77 | Total [Ah] | 0 | 0 | 0 |  | 0
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
96
97
98
99
100
101
102
103
104
105
106
107
108
109
110
111
112
113
114
115
116
117
118
119
120
121
122
123
124
125
126
127
128
129
130
131
132
133
134
135
136
137
138
139
140
141
142
143
144
145
146
147
148
149
150
151
152
153
154
155
156
157
158
159
160
161
162
163
164
165
166
167
168
169
170
171
172
173
174
175
176
177
178
179
180
181
182
183
184
185
186
187
188
189
190
191
192
193
194
195
196
197
198
199
200
201
202
203
204
205
206
207
208
209
210
211
212
213
214
215
216
217
218
219
220
221
222
223
224
225
226
227
228
229
230
231
232
233
234
235
236
237
238
239
240
241
242
243
244
245
246
247
248
249
250
251
252
253
254
255
256
257
258
259
260
261
262
263
264
265
266
267
268
269
270
271
272
273
274
275
276
277
278
279
280
281
282
283
284
285
286
287
288
289
290
291
292
293
294
295
296
297
298
299
300
301
302
303
304
305
306
307
308
309
310
311
312
313
314
315
316
317
318
319
320
321
322
323
324
325
326
327
328
329
330
331
332
333
334
335
336
337
338
339
340
341
342
343
344
345
346
347
348
349
350
351
352
353
354
355
356
357
358
359
360
361
362
363
364
365
366
367
368
369
370
371
372
373
374
375
376
377
378
379
380
381
382
383
384
385
386
387
388
389
390
391
392
393
394
395
396
397
398
399
400
401
402
403
404
405
406
407
408
409
410
411
412
413
414
415
416
417
418
419
420
421
422
423
424
425
426
427
428
429
430
431
432
433
434
435
436
437
438
439
440
441
442
443
444
445
446
447
448
449
450
451
452
453
454
455
456
457
458
459
460
461
462
463
464
465
466
467
468
469
470
471
472
473
474
475
476
477
478
479
480
481
482
483
484
485
486
487
488
489
490
491
492
493
494
495
496
497
498
499
500
501
502
503
504
505
506
507
508
509
510
511
512
513
514
515
516
517
518
519
520
521
522
523
524
525
526
527
528
529
530
531
532
533
534
535
536
537
538
539
540
541
542
543
544
545
546
547
548
549
550
551
552
553
554
555
556
557
558
559
560
561
562
563
564
565
566
567
568
569
570
571
572
573
574
575
576
577
578
579
580
581
582
583
584
585
586
587
588
589
590
591
592
593
594
595
596
597
598
599
600
601
602
603
604
605
606
607
608
609
610
611
612
613
614
615
616
617
618
619
620
621
622
623
624
625
626
627
628
629
630
631
632
633
634
635
636
637
638
639
640
641
642
643
644
645
646
647
648
649
650
651
652
653
654
655
656
657
658
659
660
661
662
663
664
665
666
667
668
669
670
671
672
673
674
675
676
677
678
679
680
681
682
683
684
685
686
687
688
689
690
691
692
693
694
695
696
697
698
699
700
750
800
850
900
950
1000
1050
1100
1150
1200
1250
1300
1350
1400
1450
1500
1550
1600
1650
1700
1750
1800
1850
1900
1950
2000
2050
2100
2150
2200
2250
2300
2350
2400
2450
2500
2550
2600
2650
2700
2750
2800
2850
2900
2950
3000
3050
3100
3150
3200
3250
3300
3350
3400
3450
3500
3550
3600
3650
3700
3750
3800
3850
3900
3950
4000
4050
4100
4150
4200
4250
4300
4350
4400
4450
4500
4550
4600
4650
4700
4750
4800
4850
4900
4950
5000
5050
5100
5150
5200
5250
5300
5350
5400
5450
5500

## Translation (hidden)
English | Selected translation | 中文 | Deutsch | English | Français | Italiano | Nederlands
English
3
HEADER | HEADER | Tab Index | Überschrift | HEADER | Tab Index | Intestazione | HEADER
Language: | Language: | 语言： | Sprache: | Language: | Langue: | Lingua: | Taal:
Date: | Date: | 日期： | Datum: | Date: | Date: | Data: | Datum:
DD-MM-YYYY | DD-MM-YYYY | DD-MM-YYYY | TT-MM-JJJJ | DD-MM-YYYY | JJ-MM-AAAA | GG-MM-AAAA | DD-MM-JJJJ
Project: | Project: | 项目： | Projekt: | Project: | Projet: | Progetto: | Projekt:
NAME | NAME | 名称 | NAME | NAME | NOM | NOME | NAAM
PRAESENSA | PRAESENSA | PRAESENSA | PRAESENSA | PRAESENSA | PRAESENSA | PRAESENSA | PRAESENSA
Power calculator | Power calculator | 功耗计算器 | Power Calculator | Power calculator | Power calculator | Power calculator | Power calculator
V1.3
Requirements | Requirements | Requirements | Anforderungen | Requirements | Requirements | Requisiti | Vereisten
Battery Operation Requirements | Battery Operation Requirements | 电池运行要求 | Anforderungen im Batteriebetrieb | Battery Operation Requirements | Prérequis batteries | Caratteristiche operative della batteria | Accu Operationele Vereisten
Time in quiescent condition | Time in quiescent condition | 待机时间 | Überbrückungszeit | Time in quiescent condition | Temps en condition de repos | Tempo in condizioni di riposo | Tijd in rust toestand
Supervision | Supervision | 状态监测 | Überwachung | Supervision | Supervision active? | La supervisione è attiva?? | Supervisie
Amplifier & EoL | Amplifier & EoL | 功放 & EoL线路终端 | Verstärker & EoL | Amplifier & EoL | Amplificateur & fin de ligne | Amplificatore e fine linea | Versterker & EoL
hour | hour | 小时 | h | hour | heure | ore | uur
Idle (no audio) | Idle (no audio) | 空闲 (无音频) | Leerlauf (kein Audio) | Idle (no audio) | Attente (pas d'audio) | Idle (no audio) | In rust (geen audio)
Speech | Speech | 语音 | Sprache | Speech | Voix | Parlato | Spraak
Time in evacuation condition | Time in evacuation condition | 疏散时间 | Evakuierungszeit | Time in evacuation condition | Temps en condition d'évacuation | Tempo in condizioni di evacuazione | Tijd in evacuatie toestand
min. | min. | 分钟 | min. | min. | min. | min. | min.
Alarm tone duty cycle | Alarm tone duty cycle | 报警音周期 | Alarmsignal-Betriebszyklus | Alarm tone duty cycle | Cycle tonalité d'alarme | Ciclo di funzionamento tono di allarme | Alarmtoon duty cycle
Safety factor (tolerance, temperature) | Safety factor (tolerance, temperature) | 安全系数 (公差、温度) | Sicherheitsfaktor (Toleranz, Temperatur) | Safety factor (tolerance, temperature) | Marge de sécurité (tolérance, température) | Fattore di sicurezza (tolleranza, temp.) | Veiligheidsfactor (tolerantie, temperatuur)
% | % | % | % | % | % | % | %
Description | Description | 描述 | Beschreibung | Description | Description | Descrizione | Beschrijving
Device: | Device | 设备 | Systemkomponente | Device | Appareil | Apparato | Apparaat
USED: | Used: | 使用 / | Aktiv: | Used: | Utilisé: | Utilizzato: | Gebruikt:
Quantity | Quantity | 数量 | Menge | Quantity | Quantité | Quantità | Hoeveel- heid
System controller | System controller | 系统控制器 | Systemcontroller | System controller | Contrôleur système | Controllore di sistema | Systeemcontroller
PRA-SCx | PRA-SCx | PRA-SCx | PRA-SCx | PRA-SCx | PRA-SCx | PRA-SCx | PRA-SCx
Multifunction Power Supply | Multifunction Power Supply | 多功能电源 | Multifunktionale Stromversorgung | Multifunction Power Supply | Alimentation multifonctions | Alimentatore Multifunzione | Multifunctionele voeding
PRA-MPS3 | PRA-MPS3 | PRA-MPS3 | PRA-MPS3 | PRA-MPS3 | PRA-MPS3 | PRA-MPS3 | PRA-MPS3
24 VDC output | 24 VDC output | 24 VDC 供电输出 | 24 VDC Ausgang | 24 VDC output | 24 VDC sortie | 24 VDC uscita | 24 VDC uitgang
48 VDC output 1 | 48 VDC output 1 | 48 VDC 供电输出 1 | 48 VDC Ausgang 1 | 48 VDC output 1 | 48 VDC sortie 1 | 48 VDC uscita 1 | 48 VDC uitgang 1
48 VDC output 2 | 48 VDC output 2 | 48 VDC 供电输出 2 | 48 VDC Ausgang 2 | 48 VDC output 2 | 48 VDC sortie 2 | 48 VDC uscita 2 | 48 VDC uitgang 2
48 VDC output 3 | 48 VDC output 3 | 48 VDC 供电输出 3 | 48 VDC Ausgang 3 | 48 VDC output 3 | 48 VDC sortie 3 | 48 VDC uscita 3 | 48 VDC uitgang 3
Active Ethernet ports on MPS [#] | Active Ethernet ports on MPS [#] | 多功能电源上已使用的以太网接口 [#] | Aktive Ethernet-Ports der MPS [#] | Active Ethernet ports on MPS [#] | Port Ethernet actif [#] | Porta Ethernet attive [#] | Actieve Ethernet poorten op MPS [#]
Active SFP port on MPS [#] | Active SFP port on MPS [#] | 多功能电源上已使用的SFP接口 [#] | Aktive SFP-Ports der MPS [#] | Active SFP port on MPS [#] | Port SFP actif [#] | Porta SFP attive [#] | Actieve SFP poort op MPS [#]
Active Ethernet ports on system controller [#] | Active Ethernet ports on system controller [#] | 系统控制器上已使用的以太网接口 [#] | Aktive Ethernet-Ports des Systemcontrollers [#] | Active Ethernet ports on system controller [#] | Ports Ethernet actifs [#] | Porte Ethernet attive [#] | Actieve Ethernet poorten op systeemcontroller [#]
Active Ethernet ports on amplifier [#] | Active Ethernet ports on amplifier [#] | 功放上已启用的以太网接口 [#] | Aktive Ethernet-Ports des Verstärkers [#] | Active Ethernet ports on amplifier [#] | Ports Ethernet actifs [#] | Porte Ethernet attive [#] | Actieve Ethernet poorten op versterker [#]
Active Ethernet ports on switch [#] | Active Ethernet ports on switch [#] | 交换机上已启用的以太网接口 [#] | Aktive Ethernet-Ports des Switch [#] | Active Ethernet ports on switch [#] | Ports Ethernet actifs [#] | Porte Ethernet attive [#] | Actieve Ethernet poorten op switch [#]
Active SFP ports on switch [#] | Active SFP ports on switch [#] | 交换机上已启用的SFP接口 [#] | Aktive SFP-Ports des Switch [#] | Active SFP ports on switch [#] | Ports SFP actifs [#] | Porte SFP attive [#] | Actieve SFP poorten op switch [#]
Total PoE load 3rd party devices [watt] | Total PoE load 3rd party devices [watt] | 第三方设备的总PoE负载 [W] | PoE-Gesamtlast 3rd-Party-Komponenten [W] | Total PoE load 3rd party devices [watt] | Charge totale PoE (produits tiers) [W] | Carico Poe totale di apparati di terze parti [W] | PoE vermogen 3rd party apparaat [W]
Total loudspeaker load [W] | Total loudspeaker load [W] | 总扬声器负载 [W] | Gesamtlautsprecherlast [W] | Total loudspeaker load [W] | Charge totale haut-parleurs [W] | Carico totale degli altoparlanti [W] | Totale luidsprekerbelasting [W]
Maximum current @24V [mA] | Maximum current @24V [mA] | 最大电流 @24V [mA] | Maximaler Strom @24V [mA] | Maximum current @24V [mA] | Courant maximumt @24V [mA] | Corrente massima @24V [mA] | Maximale stroom @24V [mA]
Current in quiescent mode @48V [mA] | Current in quiescent mode @48V [mA] | 静态模式下的电流 @48V [mA] | Strom im Ruhezustand @48V [mA] | Current in quiescent mode @48V [mA] | Courant de veille @48V [mA] | Corrente nel modo inattivo @48V [mA] | Stroom in rust toestand @48V [mA]
Current during speech @48V [mA] | Current during speech @48V [mA] | 语音播报时的电流 @48V [mA] | Strom während Durchsage @48V [mA] | Current during speech @48V [mA] | Courant diffusion vocale @48V [mA] | Corrente durante la chiamata @48V [mA] | Stroom tijdens spraak @48V [mA]
Current during alarm @48V [mA] | Current during alarm @48V [mA] | 报警时的电流 @48V [mA] | Strom während Alarmierung @48V [mA] | Current during alarm @48V [mA] | Courant diffusion alarme @48V [mA] | Corrente durante l'allarme @48V [mA] | Stroom tijdens alarm @48V [mA]
Call station | Call station | 桌面式 / 挂墙式呼叫站 | Sprechstelle | Call station | Pupitre | Stazione di chiamata | Oproeppost
PRA-CSLx | PRA-CSLx | PRA-CSLx | PRA-CSLx | PRA-CSLx | PRA-CSLx | PRA-CSLx | PRA-CSLx
Desktop call station | Desktop call station | 桌面式呼叫站 | Desktop LCD Sprechstelle | Desktop call station | Pupitre bureau | Stazione di chiamata da tavolo | Bureaublad oproeppost
PRA-CSLD [#] | PRA-CSLD [#] | PRA-CSLD [#] | PRA-CSLD [#] | PRA-CSLD [#] | PRA-CSLD [#] | PRA-CSLD [#] | PRA-CSLD [#]
Wallmount callstation | Wallmount callstation | 挂墙式呼叫站 | Wand LCD Sprechstelle | Wallmount callstation | Pupitre mural | Stazione di chiamata da parete | Wandmontage oproeppost
PRA-CSLW [#] | PRA-CSLW [#] | PRA-CSLW [#] | PRA-CSLW [#] | PRA-CSLW [#] | PRA-CSLW | PRA-CSLW [#] | PRA-CSLW [#]
Call station extension | Call station extension | 呼叫站扩展键盘 | Sprechstellenerweiterung | Call station extension | Extension pupitre [#] | Estensione della stazione di chiamata | Oproeppost extensie
PRA-CSE [#] | PRA-CSE [#] | PRA-CSE [#] | PRA-CSE [#] | PRA-CSE [#] | PRA-CSE | PRA-CSE [#] | PRA-CSE [#]
Active PoE ports (total of all call stations) [#] | Active PoE ports (total of all call stations) [#] | 已启用的PoE接口 (所有呼叫站总计) [#] | Aktive PoE-Ports (Summe aller Sprechstellen) [#] | Active PoE ports (total of all call stations) [#] | Ports PoE actifs (total des pupitres) [#] | Porte PoE attive (totale delle stazione di chiamata) [#] | Actieve PoE poorten (totaal van alle oproepposten) [#]
Call stations with class Emergency [#] | Call stations with class Emergency [#] | 配置为紧急呼叫站的数量 [#] | Alarmierungsrelevante Sprechstelle(n) [#] | Call stations with class Emergency [#] | Pupitre avec option d'alarme [#] | Stazioni di chiamata con opzione allarme [#] | Oproeppost met alarm optie [#]
Ambient noise sensor | Ambient noise sensor | 环境噪声传感器 | Umgebungsgeräuschsensor | Ambient noise sensor | Capteur de bruit ambiant | Sensore di rumore ambiente | Meetmicrofoon voor omgevingsgeluid
PRA-ANS | PRA-ANS | PRA-ANS | PRA-ANS | PRA-ANS | PRA-ANS | PRA-ANS | PRA-ANS
Active PRA-ANS PoE ports on MPS and switch [#] | Active PRA-ANS PoE ports on MPS and switch [#] | 多功能电源和交换机上已启用的PRA-ANS PoE接口 [#] | Aktive PRA-ANS PoE-ports an MPS und Switch [#] | Active PRA-ANS PoE ports on MPS and switch [#] | Ports PoE actifs des MPS et switchs pour les PRA-ANS | Porte PoE PNA-ANS attive su MPS e switch [#] | Actieve PRA-ANS PoE poorten op MPS en switch [#]
Control interface module | Control interface module | 控制接口模块 | Steuerungs-Interfacemodul | Control interface module | Module d'interface de contrôle | Modulo di interfaccia di controllo | Besturingsinterfacemodule
PRA-IM16C8 | PRA-IM16C8 | PRA-IM16C8 | PRA-IM16C8 | PRA-IM16C8 | PRA-IM16C8 | PRA-IM16C8 | PRA-IM16C8
Active PRA-IM16C8 PoE ports on MPS and switch [#] | Active PRA-IM16C8 PoE ports on MPS and switch [#] | 多功能电源和交换机上已启用的PRA-IM16C8 PoE接口 [#] | Aktive PRA-IM16C8 PoE-ports an MPS und Switch [#] | Active PRA-IM16C8 PoE ports on MPS and switch [#] | Ports PoE actifs des MPS et switchs pour les PRA-IM16C8 | Porte PoE PNA-IM16C8 attive su MPS e switch [#] | Actieve PRA-IM16C8 PoE poorten op MPS en switch [#]
Wall control panel | Wall control panel | 墙装控制面板 | Wandbedienfeld | Wall control panel | La console murale | Pannello di controllo | Wandpaneel
PRA-WCP-xx | PRA-WCP-xx | PRA-WCP-xx | PRA-WCP-xx | PRA-WCP-xx | PRA-WCP-xx | PRA-WCP-xx | PRA-WCP-xx
Active PRA-WCP-xx PoE ports on MPS and switch [#] | Active PRA-WCP-xx PoE ports on MPS and switch [#] | 多功能电源和交换机上已启用的PRA-WCP-xx PoE接口 [#] | Aktive PRA-WCP-xx PoE-ports an MPS und Switch [#] | Active PRA-WCP-xx PoE ports on MPS and switch [#] | Ports PoE actifs des MPS et switchs pour les PRA-WCP-xx | Porte PoE PNA-WCP-xx attive su MPS e switch [#] | Actieve PRA-WCP-xx PoE poorten op MPS en switch [#]
Notification text | Notification text | Notification text | Hinweistext | Notification text | Notification text | Notifica di testo | Notification text
Add at least one call station | Add at least one call station | 至少添加一台呼叫站 | Fügen Sie mindestens eine Sprechstelle hinzu | Add at least one call station | Ajouter au moins un pupitre | Aggiungere almeno una stazione di chiamata | Voeg minstens 1 oproeppost toe
Note: each MPS has 2 PoE ports! | Note: each MPS has 2 PoE ports! | 注：每台多功能电源具有2个PoE接口 | Hinweis: Jede MPS besitzt 2 PoE-Ports! | Note: each MPS has 2 PoE ports! | Note:chaque MPS a 2 ports PoE! | Nota: ciascuna MPS ha 2 porte PoE! | Let op: elke MPS heeft 2 PoE poorten!
Additional PoE ports are required (add e.g. a switch). | Additional PoE ports are required (add e.g. a switch). | 需要额外的PoE接口 (例如：增加第三方交换机) | Zusätzliche PoE-Ports notwendig (z.B. Switch hinzufügen). | Additional PoE ports are required (add e.g. a switch). | Des ports PoE additionnels sont requis. | Servono porte PoE addizionali (Es: aggiungere uno switch) | Extra PoE poorten zijn nodig (voeg bijv. een switch toe).
Maximum amount of extensions per call station is 4. | Maximum amount of extensions per call station is 4. | 每台呼叫站最多可以连接4个扩展键盘 | Max. Anzahl der Erweiterungen pro Sprechstelle ist 4. | Maximum amount of extensions per call station is 4. | Le nombre maximum d'extension par pupitre est 4. | Il massimo numero di estensioni per call station è 4 | Maximale aantal extensies per oproeppost is 4.
Minimum amount of PoE ports per call station is 1. | Minimum amount of PoE ports per call station is 1. | 每台呼叫站最少需要占用1个PoE接口 | Pro Sprechstelle wird mindestens 1 PoE-Port benötigt. | Minimum amount of PoE ports per call station is 1. | Le nombre minimum de port PoE par pupitre est 1. | Il numero minimo di porte PoE per stazione di chiamata è 1. | Minimale hoeveelheid PoE poorten per oproeppost is 1.
Maximum amount of PoE ports per call station is 2. | Maximum amount of PoE ports per call station is 2. | 每台呼叫站最多可以占用2个PoE接口 | Pro Sprechstelle können maximal 2 PoE-Ports genutzt werden. | Maximum amount of PoE ports per call station is 2. | Le nombre maximum de port PoE par pupitre est 2. | Il numero Massimo di porte PoE per stazione di chiamata è 2. | Maximale hoeveelheid PoE poorten per oproeppost is 2.
Emergency class exceeds amount of call stations. | Emergency class exceeds amount of call stations. | 紧急呼叫站的数量超过了呼叫站的总数 | Es gibt mehr Notfallsprechstellen als verfügbare Sprechstellen. | Emergency class exceeds amount of call stations. | Le nombre d'option d'alarme dépasse le nombre de pupitres indiqué. | L'opzione allarme supera il numero delle stazioni di chiamata | Alarm optie overschrijdt aantal oproepposten.
Supported battery capacity is between 100Ah and 230Ah! | Supported battery capacity is between 100Ah and 230Ah! | 支持的电池容量在100Ah和230Ah之间 | Die zulässige Batteriekapazität liegt zwischen 100Ah und 230Ah! | Supported battery capacity is between 100Ah and 230Ah! | La capacité batterie supportée est comprise entre 100Ah et 230Ah! | La capacità della batteria supportata è tra 100Ah and 230Ah! | Ondersteunde accu capaciteit is tussen 100Ah and 230Ah!
The maximum battery current of 90A is exceeded! | The maximum battery current of 90A is exceeded! | 已超过最大电池电流90A！ | Der maximale Batteriestrom von 90A wird überschritten! | The maximum battery current of 90A is exceeded! | Le courant maximum de 90A est dépassé! | La corrente di batteria massima di 90A è stata superata! | De maximale accu stroom van 90A is overschreden!
This tool calculates the power requirements for a PRAESENSA system. It calculates up to 6 clusters. A cluster consists of one PRA-MPS3 and the connected devices to be supplied with power. Use the safety factor in the calculation of the battery capacity to compensate the tolerances of battery brands and types. Please also check the rack space requirements for the calculated battery types. For each additional rack a new calculation has to be made. | This tool calculates the power requirements for a PRAESENSA system. It calculates up to 6 clusters. A cluster consists of one PRA-MPS3 and the connected devices to be supplied with power. Use the safety factor in the calculation of the battery capacity to compensate the tolerances of battery brands and types. Please also check the rack space requirements for the calculated battery types. For each additional rack a new calculation has to be made. | 该工具可以计算出PRAESENSA系统的功率需求。它最多可以计算6个群组，一个群组包含一台PRA-MPS3和由其供电的相关设备。 在计算电池容量时使用安全系数来补偿电池品牌和类型的公差。另外，需要检查所计算的电池类型对机柜空间的要求。对于每增加一个机柜，必须创建一个新的计算表。 | Der PRAESENSA-Powercalculator berechnet den Leistungsbedarf für ein PRAESENSA-System. Es berechnet bis zu 6 Cluster. Ein Cluster besteht aus einem PRA-MPS3 und den angeschlossenen Systemkomponenten, die mit Strom versorgt werden sollen. Verwenden Sie den Sicherheitsfaktor bei der Berechnung der Batteriekapazität, um die Toleranzen von Batterieherstellern und -typen auszugleichen. Bitte überprüfen Sie auch den Platzbedarf im 19“-Rack für die berechneten Batterietypen. Für jedes weitere 19“-Rack muss eine neue Berechnung durchgeführt werden. | This tool calculates the power requirements for a PRAESENSA system. It calculates up to 6 clusters. A cluster consists of one PRA-MPS3 and the connected devices to be supplied with power. Use the safety factor in the calculation of the battery capacity to compensate the tolerances of battery brands and types. Please also check the rack space requirements for the calculated battery types. For each additional rack a new calculation has to be made. | Cet outil calcule les besoins en puissances batteries nécessaires pour un système PRAESENSA. Il calcule jusqu'à 6 clusters. Un cluster est composé d'un PRA-MPS3 et des appareils connectés à alimenter. Utilisez le facteur de sécurité dans le calcul de la capacité de la batterie pour compenser les tolérances des marques et types de batteries. Veuillez également vérifier l'espace requis pour les types de batteries calculés. Pour chaque rack supplémentaire, un nouveau calcul doit être effectué. | Questo strumento calcola i requisiti di alimentazione per un sistema PRAESENSA. Calcola fino a 6 cluster. Un cluster è composto da un PRA-MPS3 e dai dispositivi collegati da alimentare. Utilizzare il fattore di sicurezza nel calcolo della capacità della batteria per compensare le tolleranze di marche e tipi di batterie. Controllare anche i requisiti di spazio su rack per i tipi di batteria calcolati. Per ogni rack aggiuntivo è necessario effettuare un nuovo calcolo. | Deze tool berekent de stroomvereisten die nodig zijn voor een PRAESENSA systeem. Er kan een berekening worden gemaakt voor maximaal 6 clusters. Elk cluster bestaat uit een PRA-MPS3 en de aangesloten apparaten die van stroom moeten worden voorzien. Gebruik de veiligheidsfactor bij het berekenen van de accucapaciteit om de toleranties van accumerken en -typen te compenseren. Controleer ook aub de benodigde ruimte in een rek voor de gebruikte accutypes. Voor elk extra rek moet een nieuwe berekening gemaakt worden.
Special Note: Maximum battery current must be observed while it highly varies among different battery types. | Special Note: Maximum battery current must be observed while it highly varies among different battery types. | 特别注意：应注意电池的最大放电电流，因为不同类型的电池具有很大的差异。 | Hinweis: Bitte beachten Sie den maximalen Entladestrom der Batterie, da dieser je nach Batterietyp stark variieren kann. | Special Note: Maximum battery current must be observed while it highly varies among different battery types. | Note spéciale: Le courant maximum de décharge de batterie doit être verifié car il varie fortement d'un type de batterie à l'autre. | Nota speciale: La massima corrente di scarica della batteria deve essere osservata considerando che varia notevolmente tra i diversi tipi di batteria. | Speciale opmerking: Neem de maximale accu ontladingsstroom in acht aangezien deze aanzienlijk varieert tussen verschillende type accu's.
|  | 免责条款： | Haftungsausschluss |  | Exclusion de responsabilité | Esclusione di responsabilità | Uitsluiting van aansprakelijkheid
The Power calculator serves as a support tool only. It cannot substitute professional advice from technical experts. For further details, our sales and support team will be happy to assist. Bosch does not warrant that the tool will fulfill any specific or general user requirement and disclaims any warranty for fitness for a specific purpose. To the extent permitted by law, Bosch will not accept any liability for any loss, damage or other consequences resulting from the use of the tool. | The Power calculator serves as a support tool only. It cannot substitute professional advice from technical experts. For further details, our sales and support team will be happy to assist. Bosch does not warrant that the tool will fulfill any specific or general user requirement and disclaims any warranty for fitness for a specific purpose. To the extent permitted by law, Bosch will not accept any liability for any loss, damage or other consequences resulting from the use of the tool. | 功率计算器仅作为一个支持工具，不能代替技术专家的专业建议。如需了解更多详情，我们的销售和技术支持团队将很乐意为您提供帮助。博世不保证该工具能满足任何特定或一般用户的要求，也不保证该工具适用于某个特定用途。在法律允许的范围内，博世不承担任何因使用该工具而导致的任何损失、损坏或其他后果。 | Der PRAESENSA-Powercalculator dient lediglich als unterstützendes Hilfsmittel. Er kann die professionelle Beratung durch technische Experten nicht ersetzen. Wir weisen ausdrücklich darauf hin, dass alle Angaben ohne Gewähr sind und jegliche Haftung durch fehlerhafte, unvollständige oder veraltete Informationen durch Bosch ausgeschlossen sind. | The Power calculator serves as a support tool only. It cannot substitute professional advice from technical experts. For further details, our sales and support team will be happy to assist. Bosch does not warrant that the tool will fulfill any specific or general user requirement and disclaims any warranty for fitness for a specific purpose. To the extent permitted by law, Bosch will not accept any liability for any loss, damage or other consequences resulting from the use of the tool. | Le calculateur sert en tant qu’outil d'aide au dimensionnement des capacités batteries . Il ne peut pas remplacer les conseils professionnels d'experts techniques. Pour plus de détails, notre équipe commerciale et technique se fera un plaisir de vous aider. Bosch ne garantit pas que l'outil satisfera à toutes exigences spécifiques ou générales de l'utilisateur et décline toutes garanties d'adéquation à un usage spécifique. Dans la mesure permise par la loi, Bosch décline toute responsabilité pour toute pertes, dommages ou tout autres conséquences résultant de l'utilisation de cet outil. | Il Power Calculator serve solo come strumento di supporto. Non può sostituire la consulenza professionale di esperti tecnici. Per ulteriori dettagli, il nostro team di vendita e assistenza sarà lieto di aiutarvi. Bosch non garantisce che lo strumento soddisferà qualsiasi requisito specifico o generale dell'utente e declina qualsiasi garanzia di idoneità per uno scopo specifico. Nella misura consentita dalla legge, Bosch declina qualsiasi responsabilità per eventuali perdite, danni o altre conseguenze derivanti dall'uso dello strumento. | De Power calculator dient alleen als ondersteuningsinstrument. Het kan professioneel advies van technische experts niet vervangen. Voor meer informatie helpt ons verkoop- en ondersteuningsteam u graag verder. Bosch garandeert niet dat deze tool zal voldoen aan een specifieke of algemene gebruikersvereiste en wijst elke garantie van toepassing voor een specifiek doel af. Voor zover wettelijk toegestaan, aanvaardt Bosch geen enkele aansprakelijkheid voor verlies, schade of andere gevolgen als gevolg van het gebruik van deze tool.
WRONG DATA ENTRIE(S) > CHECK ALL QUANTITIES !!! | WRONG DATA ENTRIE(S) > CHECK ALL QUANTITIES !!! | 数据输入错误 > 检查所有项目的数量！ | Falsche Dateneingabe(n) > Alle Mengeneingaben überprüfen! | WRONG DATA ENTRIE(S) > CHECK ALL QUANTITIES !!! | ENTREE DE DONNEES ERRONNEE (S) > VERIFIEZ LES QUANTITES !!! | INSERIMENTO DATI ERRATO > VERIFICARE TUTTE LE QUANTITA' !!! | ONJUISTE DATA > CONTROLEER ALLE INGEVOERDE HOEVEELHEDEN !!!
Min. 1 | Min. 1 | 最小值 1 | Min. 1 | Min. 1 | Min. 1 | Min. 1 | Min. 1
Max. 1 | Max. 1 | 最大值 1 | Max. 1 | Max. 1 | Max. 1 | Max. 1 | Max. 1
Max. 2 | Max. 2 | 最大值 2 | Max. 2 | Max. 2 | Max. 2 | Max. 2 | Max. 2
Max. 5 | Max. 5 | 最大值 5 | Max. 5 | Max. 5 | Max. 5 | Max. 5 | Max. 5
Max. 8 | Max. 8 | 最大值 8 | Max. 8 | Max. 8 | Max. 8 | Max. 8 | Max. 8
Max. 120 | Max. 120 | 最大值 120 | Max. 120 | Max. 120 | Max. 120 | Max. 120 | Max. 120
Max. 600 | Max. 600 | 最大值 600 | Max. 600 | Max. 600 | Max. 600 | Max. 600 | Max. 600
Max. 700 | Max. 700 | 最大值 700 | Max. 700 | Max. 700 | Max. 700 | Max. 700 | Max. 700
Max. 5500 | Max. 5500 | 最大值 5500 | Max. 5500 | Max. 5500 | Max. 5500 | Max. 5500 | Max. 5500
Drop down menus - dont change! | Drop down menus | Drop down menus - don't change! | Dropdown-Menüs - nicht änderen! | Drop down menus | Drop down menus - ne change pas! | Menu a discesa - non cambiare! | Drop down menus - niet veranderen!
- | - | - | - | - | - | - | -
YES | YES | 是 | JA | YES | Oui | SI | JA
NO | NO | 否 | NEIN | NO | NON | NO | NEE
- | - | - | - | - | - | - | -
PRA-SCx | PRA-SCx | PRA-SCx | PRA-SCx | PRA-SCx | PRA-SCx | PRA-SCx | PRA-SCx
3rd-Party | 3rd-Party | 3rd-Party | 3rd-Party | 3rd-Party | 3rd-Party | 3rd-Party | 3rd-Party
- | - | - | - | - | - | - | -
PRA-AD604 | PRA-AD604 | PRA-AD604 | PRA-AD604 | PRA-AD604 | PRA-AD604 | PRA-AD604 | PRA-AD604
PRA-AD608 | PRA-AD608 | PRA-AD608 | PRA-AD608 | PRA-AD608 | PRA-AD608 | PRA-AD608 | PRA-AD608
PRA-ES8P2S | PRA-ES8P2S | PRA-ES8P2S | PRA-ES8P2S | PRA-ES8P2S | PRA-ES8P2S | PRA-ES8P2S | PRA-ES8P2S
3rd-Party | 3rd-Party | 3rd-Party | 3rd-Party | 3rd-Party | 3rd-Party | 3rd-Party | 3rd-Party
Calculation | Calculation | Calculation | Berechnung | Calculation | Calculation | Calcolatore | Calculation
Cluster | Cluster | 群组 | Cluster | Cluster | Cluster | Cluster | Cluster
Required battery capacity including safety factor (minimum 100 Ah - maximum 230 Ah) | Required battery capacity including safety factor (minimum 100 Ah - maximum 230 Ah) | 所需的电池容量，包含安全系数 (最小100 Ah - 最大230 Ah) | Erforderliche Batteriekapazität inkl. Sicherheitsfaktor (Minimum 100 Ah - Maximum 230 Ah) | Required battery capacity including safety factor (minimum 100 Ah - maximum 230 Ah) | Capacité batterie requise incluant la marge de sécurité (minimum 100 Ah - maximum 230 Ah) | Capacità della batteria richiesta incl. fattore di sicurezza (minimo 100 Ah - massimo 230 Ah) | Vereiste accu capaciteit inclusief veiligheidsmarge (minimaal 100 Ah - maximaal 230 Ah)
Ah | Ah | Ah | Ah | Ah | Ah | Ah | Ah
Maximum battery current (check battery specification) | Maximum battery current (check battery specification) | 最大电池电流 (请复核电池的技术规格书) | Maximaler Batteriestrom (Bitte Batteriespezifikation beachten.) | Maximum battery current (check battery specification) | Courant de batterie maximum | Massima corrente della batteria | Maximale accu stroom (controleer de accu specificatie)
A | A | A | A | A | A | A | A
Mains current draw at 230 VAC (during alarm and bulk charging) | Mains current draw at 230 VAC (during alarm and bulk charging) | 市电电流消耗 230 VAC (在报警和高速充电期间) | Netzstromaufnahme @ 230 VAC (bei Alarmierung und Hauptladung) | Mains current draw at 230 VAC (during alarm and bulk charging) | Courant secteur sur 230 VAC (durant alarme et charge forte) | Assorbimento di corrente a 230 V CA (durante l'allarme e la carica complessiva) | Stroomopname uit lichtnet - 230 VAC (tijdens alarm en bulk laden)
Mains current draw at 115 VAC (during alarm and bulk charging) | Mains current draw at 115 VAC (during alarm and bulk charging) | 市电电流消耗 115 VAC (在报警和高速充电期间) | Netzstromaufnahme @ 115 VAC (bei Alarmierung und Hauptladung) | Mains current draw at 115 VAC (during alarm and bulk charging) | Courant secteur sur 115 VAC (durant alarme et charge forte) | Assorbimento di corrente a 115 V CA (durante l'allarme e la carica complessiva) | Stroomopname uit lichtnet - 115 VAC (tijdens alarm en bulk laden)
Total heat loss | Total heat loss | 总热损耗 | Systemverlustleistung | Total heat loss | Calcul de perte de puissance | Calcolo della perdita di potenza | Totaal warmteverlies
(heat dissipation inside the rack)* | (heat dissipation inside the rack)* | (机架内部的散热)* | (Abwärme innerhalb des Racks) | (heat dissipation inside the rack)* | (Dissipation calorifique à l'intérieur du rack) | (dissipazione termica all'interno del rack) | (warmte dissipatie in het rack)
Idle | Idle | 待机时 | Leerlauf | Idle | Inactif | Inattivo | Inactief
Low power | Low power | 低功率 运行时 | Niedrige Leistung | Low power | Bas puissance | Potenza bassa | Laag vermogen
Full power | Full power | 全功率 运行时 | Volle Leistung | Full power | Pleine puissance | Potenza massima | Vol vermogen
Total power loss of amplifiers | Total power loss of amplifiers | 功放的总功率损耗 | Gesamtverlustleistung der Verstärker | Total power loss of amplifiers | Perte de puissance totale des amplificateurs | Perdita di potenza totale degli amplificatori | Totaal vermogensverlies van de versterkers
Total power loss of PRA-AD608 amplifiers | Total power loss of PRA-AD608 amplifiers | PRA-AD608功放的总功率损耗 | Gesamtverlustleistung der PRA-AD608 Verstärker | Total power loss of PRA-AD608 amplifiers | Perte de puissance totale des amplificateurs PRA-AD608 | Perdita di potenza totale degli amplificatori PRA-AD604 | Totaal vermogensverlies PRA-AD608 versterkers
W | W | W | W | W | W | W | W
Total heat loss | Total heat loss | 总热损耗 | Systemverlustleistung | Total heat loss | Perte de puissance système | Dissipazione di calore totale | Totaal warmteverlies
BTU/h | BTU/h | BTU/h | BTU/h | BTU/h | BTU/h | BTU/h | BTU/h
kcal/h | kcal/h | kcal/h | kcal/h | kcal/h | kcal/h | kcal/h | kcal/h
* Excluding call stations and 3rd party devices | * Excluding call stations and 3rd party devices | * 不包括呼叫站和第三方设备 | * Exklusiv Sprechstelle und Geräte von Drittanbietern | * Excluding call stations and 3rd party devices | * À l'exclusion des pupitres et des appareils tiers | * Escluse le stazioni di chiamata e i dispositivi di terze parti | * Exclusief oproepposten en apparaten van derden
Info | Info | Info | Info | Info | Info | Info | Info
USER INSTRUCTIONS | USER INSTRUCTIONS | 使用说明 | Benutzerhinweise | USER INSTRUCTIONS | INSTRUCTIONS D'UTILISATION | ISTRUZIONI D'USO | GEBRUIKSAANWIJZING
1. Start by selecting the required language above. | 1. Start by selecting the required language above. | 1. 选择所需的界面语言 | 1. Wählen Sie oben die gewünschte Sprache aus. | 1. Start by selecting the required language above. | 1. Commencez par sélectionner la langue requise ci-dessus. | 1. Selezionare la lingua richiesta in alto a dx. | 1. Selecteer om te beginnen de taal hierboven.
2. All yellow marked cells are drop down input fields (click on it). | 2. All yellow marked cells are drop down input fields (click on it). | 2. 黄色单元格是下拉菜单，请点击后选择 | 2. Alle gelb markierten Zellen sind Dropdown-Eingabefelder (bitte anklicken). | 2. All yellow marked cells are drop down input fields (click on it). | 2. Toutes les cellules marquées en jaune sont des champs de saisie déroulants (cliquez dessus). | 2. Tutte le celle contrassegnate in giallo sono campi di input a discesa (fai clic). | 2. Alle geel gemarkeerde cellen zijn invoervelden (klik er op).
3. When the text in these yellow cells is red the data has to be typed in. | 3. When the text in these yellow cells is red the data has to be typed in. | 3. 如果黄色单元格内显示红色文字，表示需要输入这个数据 | 3. Wenn der Text in diesen gelben Zellen rot angezeigt wird, müssen Sie Daten eingeben. | 3. When the text in these yellow cells is red the data has to be typed in. | 3. Lorsque le texte dans ces cellules jaunes est rouge, les données doivent être saisies. | 3. Quando il testo in queste celle gialle è rosso, è necessario digitare i dati. | 2. Wanneer de tekst in deze cellen rood is dan moet de data ingetypt worden.
4. Select the INFO tab and type in the date and project name. | 4. Select the INFO tab and type in the date, project name and battery operation requirements. | 4. 进入INFO页，输入日期、项目名称和电池运行要求 | 4. Klicken Sie auf die Registerkarte INFO und geben Sie das Datum, den Projektnamen und die Anforderungen im Batteriebetrieb ein. | 4. Select the INFO tab and type in the date, project name and battery operation requirements. | 4. Sélectionnez l'onglet INFO et saisissez la date et le nom du projet. | 4. Selezionare il tab INFO (sotto) e digitare la data e il nome del progetto. | 4. Selecteer de INFO tab aan de onderkant en vul de datum, projektnaam en de operationele eisen voor de accu in.
5. Select per cluster the tab at the bottom and fill in the required data. | 5. Select per cluster the tab at the bottom and fill in the required data. | 5. 逐一在每个群组页中填入所需的数据 | 5. Wählen Sie pro Cluster unten eine Registerkarte und geben Sie die erforderlichen Daten ein. | 5. Select per cluster the tab at the bottom and fill in the required data. | 5. Sélectionnez par système l'onglet en bas et remplissez les données requises. | 5. Selezionare per ogni cluster il relativo tab in basso e inserire i dati richiesti. | 5. Selecteer per cluster de tab aan de onderkant en vul de vereiste data in.
6. Result per cluster is displayed in the INFO tab including heat loss of the complete rack. | 6. Result per cluster is displayed in the INFO tab including heat loss of the complete rack. | 6. 每个群组的计算结果将显示在INFO页中，包含整个机柜的热损耗 | 6. Das Ergebnis pro Cluster wird unten angezeigt, einschließlich des Wärmeverlusts des gesamten Racks. | 6. Result per cluster is displayed in the INFO tab including heat loss of the complete rack. | 6. Le résultat par système est affiché ci-dessous, y compris la perte calorifique du rack complet. | 6. I risultati per cluster sono visualizzati nel tab INFO, inclusa la dissipazione di calore del rack completo. | 6. Het resultaat per cluster wordt in de INFO tab weergegeven inclusief het warmteverlies van het complete rack.
GLOSSARY | GLOSSARY | 术语表 | GLOSSAR | GLOSSARY | GLOSSAIRE | GLOSSARIO | WOORDENLIJST
when the system is powered by a power supply conforming to EN 54-4 and no other functional condition is indicated. | When the system is powered by a power supply conforming to EN 54-4 and no other functional condition is indicated. | 当系统通过一个符合EN54-4标准的电源供电，不启用任何系统功能时 | Das System wird von einer gemäß EN54-4 zertifizierten Stromversorgung gespeist und es wird kein anderer Funktionszustand angezeigt. | When the system is powered by a power supply conforming to EN 54-4 and no other functional condition is indicated. | Lorsque le système est alimenté par une alimentation conforme EN 54-4 et qu'aucune autre condition fonctionnelle n'est indiquée. | quando il sistema è alimentato da un alimentatore conforme a EN 54-4 e non sono indicate altre condizioni funzionali. | wanneer het systeem gevoed wordt door een voeding conform EN 54-4 en er geen andere functionele staat aangegeven wordt.
when the system is used for a spoken message, either live or pre-recorded, sent to all connected loudspeakers. | when the system is used for a spoken message, either live or pre-recorded, sent to all connected loudspeakers. | 当系统用于播放语音信息时，即实时人工语音或者预录语音 | Das System wird für eine Durchsage verwendet, die entweder Live oder vom Sprachspeicher an alle angeschlossenen Lautsprecherlinien übertragen wird. | when the system is used for a spoken message, either live or pre-recorded, sent to all connected loudspeakers. | Lorsque le système est utilisé pour un message parlé, en direct ou préenregistré, envoyé à tous les haut-parleurs connectés. | quando il sistema viene utilizzato per un messaggio vocale, in diretta o preregistrato, inviato a tutti gli altoparlanti collegati. | wanneer het systeem gebruikt wordt voor een gesproken bericht, zowel ingesproken als vooraf opgenomen, naar alle aangesloten luidsprekers
Maximum time interval the voice alarm system must be used for evacuation. | Maximum time interval the voice alarm system must be used for evacuation. | 播放RMS电平小于等于-9 dBFS的报警音 | Maximales Zeitintervall, in dem das Sprachalarmsystem zur Evakuierung verwendet werden muss. | Maximum time interval the voice alarm system must be used for evacuation. | Intervalle de temps maximum le système d'alarme vocale doit être utilisé pour l'évacuation. | Intervallo di tempo massimo per l'evacuazione del sistema di allarme vocale. | Maximale tijdsinterval dat het gesproken woord ontruimingssysteem gebruikt moet worden voor evacuatie.
The percentage of one period of the alarm tone in which the alarm signal is active. For example a duty cycle of 80% means that in one complete cycle of the alarm tone 80% carries an audible sound. The other 20% is silence. | The percentage of one period of the alarm tone in which the alarm signal is active. For example a duty cycle of 80% means that in one complete cycle of the alarm tone 80% carries an audible sound. The other 20% is silence. | 在一个报警周期内，报警音所占的时长百分比。例如80%表示在一个周期内，80%的时长能听到报警音，剩余20%的时长是无声状态 | Der prozentuale Anteil eines Alarmierungszyklus, in dem das Alarmsignal aktiv ist. Zum Beispiel bedeutet ein Betriebszyklus von 80%, dass in einem vollständigen Zyklus der Alarmierung 80% ein hörbares Alarmsignal übertragen wird. Die verbleibenden 20% sind stumm. | The percentage of one period of the alarm tone in which the alarm signal is active. For example a duty cycle of 80% means that in one complete cycle of the alarm tone 80% carries an audible sound. The other 20% is silence. | Pourcentage d'une période de la tonalité d'alarme pendant laquelle le signal d'alarme est actif. Par exemple, un rapport cyclique de 80% signifie que dans un cycle complet de la tonalité d'alarme, 80% porte un son audible. Les 20% restants sont le silence. | La percentuale di un periodo del tono di allarme in cui è attivo il segnale di allarme. Ad esempio, un ciclo di lavoro dell'80% significa che in un ciclo completo del tono di allarme l' 80% trasmette un suono udibile. L'altro 20% è il silenzio. | Het percentage van één periode van de alarmtoon waarin het alarmsignaal actief is. Bijvoorbeeld een duty cycle van 80% wil zeggen dat tijdens één periode van de alarmtoon 80% een hoorbaar signaal is. De overige 20% is stilte.
Additional battery capacity to compensate for aging and low temperature operation, appr. 10%, as well as reduced capacity, appr. 20%, due to fast discharge of the battery (Peukert's law). | Additional battery capacity to compensate for aging and low temperature operation, appr. 10%, as well as reduced capacity, appr. 20%, due to fast discharge of the battery (Peukert's law). | 额外的电池容量用于补偿电池老化和低温工作，通常10%用于补偿衰减的容量，20%用于补偿快速放电带来的影响 | Zusätzliche Batteriekapazität zur Kompensation von Alterung und Niedrigtemperaturbetrieb (ca. 10%), sowie reduzierte Kapazität (ca. 20%) aufgrund Schnellentladung der Batterie (Peukert-Gesetz). | Additional battery capacity to compensate for aging and low temperature operation, appr. 10%, as well as reduced capacity, appr. 20%, due to fast discharge of the battery (Peukert's law). | Capacité de batterie supplémentaire pour compenser le vieillissement et le fonctionnement à basse température, env. 10%, ainsi qu'une capacité réduite, env. 20%, en raison d'une décharge rapide de la batterie (loi de Peukert). | Capacità aggiuntiva della batteria di compensare l'invecchiamento e il funzionamento a bassa temperatura, appr. 10%, oltre alla capacità ridotta, appr. 20%, a causa della scarica rapida della batteria (legge di Peukert). | Extra accu capaciteit ter compensatie van veroudering en gebruik bij lage temperaturen, ongeveer 10%, als ook gereduceerde capaciteit, ongeveer 20%, als gevolg van snelle ontlading van de accu (Peukert's wet)
For more information about battery and heat loss calculation please read the applicable sections in chapter "System composition" of the PRAESENSA Installation manual. | For more information about battery and heat loss calculation please read the applicable sections in chapter "System composition" of the PRAESENSA Installation manual. | 请查阅PRAESENSA用户手册的“系统组件”章节，获取更多关于电池和热损耗的计算方法。 | Für weitere Informationen zur Batterie- und Wärmeverlustberechnung lesen Sie bitte die entsprechenden Abschnitte im Kapitel "Systemaufbau" des PRAESENSA-Handbuchs. | For more information about battery and heat loss calculation please read the applicable sections in chapter "System composition" of the PRAESENSA Installation manual. | Pour plus d'informations sur le calcul de batterie et de perte calorifique, veuillez lire les sections du chapitre "Composition du système" du manuel PRAESENSA. | Per ulteriori informazioni sul calcolo della perdita della batteria e della batteria, leggere le sezioni applicabili nel capitolo "Composizione del sistema" del manuale di installazione PRAESENSA. | Voor meer informatie over accu en warmteverlies berekening lees de toepasselijke secties in het hoofdstuk "System composition" van de PRAESENSA Installatie handleiding.

## Colors (hidden)
Color RGB | R | G | B
| 234 | 0 | 22
| 0 | 142 | 207
| 127 | 198 | 231
| 191 | 227 | 243
| 253 | 215 | 139
| 252 | 175 | 23 | Warning

## Description (hidden)
Revision information
Password: Bosch-EIN
V1.0
• First release
V1.1
• Corrected mains current calculation at cell H68 in the CALC_x tabs. Value will be zero when nothing is selected.
• Updated Chinese translation.
• Removed external link.
V1.2
• Corrected mains current calculation in CLUSTER tabs because it used H67 from the CALC tabs instead of H68 (was already OK in INFO tab) and updated mains current for amplifiers (Q15 and Q18)
• Added kcal/h in the heat loss calculation
• Added low power in the heat loss calculation
• Updated amplifier power consumption and heat loss, see red figures in the tables below. Changes are marked yellow in the CALC_x tabs.
• Added the option per cluster to make a choice if you use that cluster yes or no and also the choice, when YES is selected for a cluster, if you want to use the call station(s) yes or no.
• Changed notification text at call station extension, PoE port and emergency class to "Add at least one call station" once you have selected a call station with any of these options and afterwards you set the amount of call stations to zero.
• Added ANS also with option to use it yes or no
• Second update amplifier power consumption and heat loss, see shaded red figures in the tables below. Changes are marked green in the CALC_x tabs.
• Added one decimal in the quiescent condition time (INFO tab)
• Updated check for avaialble PoE ports for call stations and ANS
V1.3
• Added PRA-IM16C8 and PRA-WCP-xx (EU and US versions) to the equipment list
• Changed system controller identificator from PRA-SCL to PRA-SCx to cover the small version (power consumption parameters are identical)
• Corrected some discovered ommissions in the CALC_x worksheet formulae (some non critical total values had omitted PRA-ANS numbers)
• Updated CALC_x cell references in the description text below to reflect newly added components
PRA-ANS
Power consumption of the PRA-ANS is 1.6 W continuously, i.e. there is no sleep mode or so. On average it takes 1.9 W from the battery when connected to an Ethernet port with PoE of the MPS3, but also when it is connected to a PoE port of the switch and the switch is connected to a 48 V output of the MPS3. The approximation assumes that some 20% additional power is needed to compensate for the losses of the PoE DC/DC converter in either the MPS3 or ES8P2S. When ANS is selcted in the calculator the required power is automatically added. This means that when e.g. PoE ports from the switch are used you don't have to add the required power to the switch (same as for the call station). In case all PoE ports on the MPS and ES8P2S are in use a message will pop up: Additional PoE ports are required (add e.g. a switch). In the drop down the avaialble amount of PoE ports will be listed. If there are no PoE ports available the drop down will show the number 0. The check on avaialble PoE ports is also done for the call stations as follows: when the total amount of call stations reaches the amount of avaialble PoE ports you can't add another CST anymore (each CST requires at least one PoE port). Also when the acitve PoE ports you want to assign exceeds the amount of available PoE ports this is not possible. In theory 26 PoE ports can be used, 2 from he MPS and 3x8 from the ES8P2S switches.
PRA-IM16C8
Power consumption of the PRA-IM16C8 is 3.7 W, no sleep mode. Power drain from battery is 4.4 W, when using PoE from MPS3 or Ethernet switch powered from battery. Same as with PRA-ANS, 20% extra losses are assumed for DC/DC convertion. All required power is automatically added to the calculation once a PRA-IM16C8 is added. The number of used and available PoE ports either from MPS3 or ES8P2S is automatically handled by the tool.
PRA-WCP-xx
Power consumption of the PRA-WCP is 1.3 W, no sleep mode. Power drain from battery is 1.6 W, when using PoE from MPS3 or Ethernet switch powered from battery. Same as with PRA-ANS, 20% extra losses are assumed for DC/DC convertion. All required power is automatically added to the calculation once a PRA-WCP is added. The number of used and available PoE ports either from MPS3 or ES8P2S is automatically handled by the tool.
Technical description
General
This tool is designed for the calculation of the battery power required for a PRAESENSA system wit a maximum of 6 MPS's. It also calculates the requied mains current and power loss / heat loss.
The data used in this tool is taken from the PRAESENSA manual, see chapter called "Power consumption".
The use of macro's is not allowed. All calculations are done with formula's. Data Validation is used to create drop down lists. Conditional Formating is used to change font colors and cel colors based on applied rules.
There are three operation requirements that must be entered by the user:
1. Quiescent mode: this is the time that the system is in snooze mode
2. Alarm tones: this is the time the system will be running on full power
3. Safety factor: this is the additional battery capacity
The calculations are made per cluster. Each cluster contains at least one MPS and a battery. A maximum of three amplifiers can be connected to one MPS. A maximum of 6 MPS's will fit into a 40 RU rack including one controller.
For each cluster the configuration must be entered in the specific CLUSTER_x tab. The calculations are done in the CALC_x tab for each indivudual cluster. The final result for all clusters is presented in the INFO tab.
There are in total 17 tabs in this tool. 8 tabs are avaialble for the user and the other 9 tabs are hidden. Below a more detailed description per tab:
README
Contains a language selection, user instruction and a disclaimer on the bottom:
1. Language selection: select via the dropdown a language from the list. The list is specified by "Data Validation" The actual text is stored in the Translation tab. More details about that are in the description of the Translation tab.
2. User instructions: describes how to use the tool. Only the yellow marked cells can be accessed by the user. The rest is blocked because all tabs are protected. When you protect a sheet, right click on the tab, make sure that the Edit object is not selected otherwise objects like the logo can be selected.
3. Disclaimer: short explanation abput the tool and exlusion of liability. This part is visible in all user tabs.
INFO
Here the user can type in a data and project name as well as the three Battery Operation Requirements (Quiescent mode, Alarm tones and Safety factor).
The entered requirements for quiescent mode and alarm tones are uses in each CALC_x tab,
The safety factor is used in each CLUSTER_x tab in the required battery capacity calculation, see cell S11
Below the Battery Operation Requirements the result for each cluster is displayed. The calculations are done by formulas. The data per cluster is taken from the individual CALC_x tab.
The heat loss calculation is also done by formulas. The total power loss of all amplifiers in the system is calculated. With that figure the total heat loss within the complete rack is calculated.
For 3rd party devices 15% of the power is calculated as heat loss.
CLUSTER_x
There are 6 cluster tabs. On the left side the cluster header and the option to indicate if the cluster is used yes or no. When yes is selected two more options will appear below the header. The first one to use an MPS yes or no and the second one to use the call station yes or no..
There are three columns below the cluster header:
1. Description: description of the used device starting with the MPS. Below that the 4 outputs of the MPS3 and the call stations. These become visible when the option Used: YES for the MPS and call station are selected.
2. Device: here the user can select the actual devices connected to the MPS via the yellow marked dropdowns. There are two types of outputs on the MPS, 24 VDC and 48 VDC. The following devices can be selected:
24 VDC output:
PRA-SCL (System controller)
3rd-Party
48 VDC output:
PRA-AD604 (600 W-4 channel)
PRA-AD608 (600 W-8 channel)
PRA-ES8P2S (8xPoE + 2xSFP)
3rd-Party
For the call stations the availble devices are fixed.
3. In this column the user must select YES or NO for the MPS and Call station. When YES is selected all avaialble devices become visible and the user must enter the amount used per device via the dropdown. The list is specified by "Data Validation". When the entry is wrong an ERROR alert will pop up.
The error message contains only a space because otherwise an English text is always visible in that window. If you choose another language that would not make sense.
In the cells next to the quantity dropdown cells there is text available. The color of this text is white so you will not see it. When a wrong value in the quantity cell is present the color of the text changes to black.
This is specified by rules in "Conditional Formatting". In order to enter the rule click on the applicable cell and then on Conditional Formatting from the Home menu. On the dropdown select Manage Rules…
On the right side the result is presented in four blue bars calculated by formulas:
1. Required battery capacity incl. safety factor (min. 100Ah - max. 230Ah)
When nothing is selected the value is zero.
At the moment a device is selected the value will change to 100. This is the minimum value of the battery capacity that a MPS requires.
When more devices are added and the required battery capacity will be above 100 Ah the actual value will be displayed. At the moment the required battery capacity exceeds 230 Ah the cell will turn red.
Also the cells below the blue bar will turn red with the text "Supported battery capacity is between 100Ah and 230Ah!". The initial color of this text is white. The cells will become red as defined by a rule in Conditional Formatting.
2. Maximum battery current (check battery specification)
The maximum battery current a MPS can handle is 90 A.
At the moment the required battery current exceeds 90 Ah the cell will turn red.
Also the cells below the blue bar will turn red with the text "The maximum battery current of 90A is exceeded!". The initial color of this text is white. The cells will become red as defined by a rule in Conditional Formatting.
3. Mains current draw at 230 V AC (during alarm and maximum battery charging)
The current at 230 V AC from all devices is added up and a correction factor is applied. See CALC_x for details
4. Mains current draw at 115 V AC (during alarm and maximum battery charging)
The current at 230 V AC from all devices is added up, multiplied by 2 and a correction factor is applied. See CALC_x for details
CALC_x
In column A all digits up to 5500 are listed. They are used for the dropdown selections. 5500 is the highest current in mA an MPS output of 48 V DC can handle. Note that above 700 the numbers are increased by 50. This is done to keep the dropdown list as short as possible.
Range C7 - K40 contains the calculation data of all devices:
Column C = names of all devices
Column E = battery current in mA as specified in the PRAESENSA manual, see chapter called "Power consumption". For the quiescent state the snooze figures of te amplifiers are applicable. Note that for the 3rd-Party the values are taken from the input in the CLUSTER_x tab.
Column F = battery current in mA as specified in the PRAESENSA manual, see chapter called "Power consumption". For the alarm state the actual power figures are applicable. These are calculated with the actual loudspeaker load. Note that for the other device the values are taken from the input in the CLUSTER_x tab.
Column H = the quantity that the user enters in the CLUSTER_x tab. Note that the PRA-MPS3 quantity is by default 1. For the amplifiers and the PRA-ES8P2S the total quantity is calculated in columns M, N and O.
Column J = multiply the current from column E with the amount of deivces from column H
Column K = multiply the current from column F with the amount of deivces from column H. Note that for the amplifiers the current is calcualted per Watt added to the minmum current required at low power.
Row 42 = sum of column H, J and K. The maximum value of cells J42 and K42 is the maximum battery current.
Row 43 = sum of column H, J and K without MPS3
Cell Q7 = maximum mains current required for charging the battery. Maximum current 9A @ 14.5V. Measurements show that the mains current is higher an therefor a correction of 0.2A is added.
Cell Q16 = maximum mains current for a 4 channel amplifier PRA-AD604 (excluding Ethernet ports)
Cell Q19 = maximum mains current for a 8 channel amplifier PRA-AD608 (excluding Ethernet ports)
Cell H45 = selected quantity checks if the user has entered any quantity for a cluster. It is the sum of H10 to H40. When nothing is entered the value will be zero. This is checked in F78 in order to make sure that initially when the user has not entered anything yet all values are zero in the INFO tab.
Otherwise the required power for the MPS will be already visible because the MPS is by default set to 1.
Cells H46 and H 47 = check if all entered values by the user are within the limits. The check is done in the formula-bar. When all entries are OK the result is FALSE. When any entry is wrong the result is TRUE. In the CLUSTER_x tab this cell is checked in conditional fomatting of cell K31 to show the fault message.
Range C52 - H78 contains the final calculations taking the system requirements from the INFO tab into account:
Column C = names of all devices
Column D = battery current in Ah for the quiescent state. Multiplies the calculated values from column J with the quiescent time from cell F17 of the INFO tab. The result is divided by 1000 to convert mA to A
Column E = battery current in Ah for the alarm state. Multiplies the calculated values from column K with the evacuation time from cell F19 of the INFO tab. The result is divided by 1000 to convert mA to A
Column F = total battery current in A. The total current in quiescent state from column D and the current in alarm state from column E.
Column G = total mains curent in mA @ 230 V per device. Note that for PoE load of the PRA-ES8P2S the mains current per device is not calculated because it depends on the actual load per device. For the amplifiers use the maximum current of the PRA-AD608 for both amplifiers at 600 W lsp load.
Column H = total mains curent in mA @ 230 V. Multiply the value from one device of column G with the quantity from the corresponding column H7 to H40. For the CSE use the maximum current when all LED's are on = 100mA instead of 10mA (in G71 > F32*10)
Row 69 = sum of column cell H52:H68 times a correction of the total mains current for all devices except the call stations with the formula (1.06 x calculated value) + 0.19. This is based on the actual measurements that were performed on PRAESENSA, see result below
Row 73 = sum of column cell H70:H73 times a correction of the total mains current for the call stations with the formula (1.06 x calculated value). This is based on the actual measurements that were performed on PRAESENSA, see result below
Row 78 = sum of column D, E, F and for column H the sum of cells 69, 74,75,76 and 77. Cell F78 is the actual required battery capacity. Cell H78 is the total mains current @ 230 V required (including the mains current correction)
Relation calculations and measurements - max. power of PRA-608 (also for PRA-604)
Condition: bulk charge - Vmains = 230Vac
Configuration
MPS3 nothing connected
SCL connected to MPS3, SCL uses 5 ethernetports,the ethernetports are connected from the SCL to the 2xAD608, 1xAD604,CS and PC. The amplifiers and CS are powered externally
1 x CS + 4 x CSE & all leds enabled from all CSE. CS is powered with MPS3 with POE. Only one ETH connections of the MPS active
Switch to MPS with no PoE load connected
1 x CS + 4 x CSE & all leds enabled from all CSE. CS is powered with POE from switch. Switch is powered by 48V output from MPS3
150Wrms on 8 channels with 133Ω load & normal mode, Pink Noise as input*, both Eth with SCL connected, which is externally supplied
MPS3 delivers power to 2xAD608, 1xAD604, 2xCS and SCL. All 48V outputs are enabled and all etherports are used. Each AD608/4 delivers 150Wrms output power and has pink noise as input*
Column J42 - M52 contain the heat loss calculations. Only the rack mounted devices take part in the heat loss calculation. When only the call station section is used the heat loss will be zero. Once the MPS is also selected the heat loss of the power required for the call stations will be added.
Row 42-43 = header
Row 44-45 = column names for idle, low power and full power mode
Row 46-47 = power from battery for each mode (see manual chapter 5.4.3 Power consumption). Note that for the PRA-ES8P2S PoE load (H24), the call stations (H29-H33) and 3rd party devices (J13, J25-J27) 15% of the power is calculated as heat loss.
Row 48-49 = names of all devices
Row 50-51 = names of all devices
Translation
Contains all translations:
Column A = the initial English text
Column B = the selected language from the README tab. The actaul text will be copied from the next columns where the translation of the specific language is avaialble.
Column C onward = translations per language
Colors
Contains the used colors in this tool according to the Bosch style guide.